## school
Secondary School
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 97785.8 | 2.66 | 9.06 | 9.59 | 9.42 | Coil:Heating:Fuel | 281397.87 | Fan:VariableVolume | 0.75 | 640 | 4.07 | 3469.16 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 19887.1 | 2.84 | 9.68 | 10.24 | 10.01 | Coil:Heating:Fuel | 57228.96 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 95819.5 | 2.65 | 9.05 | 9.58 | 9.4 | Coil:Heating:Fuel | 275739.54 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 95819.5 | 2.65 | 9.05 | 9.58 | 9.4 | Coil:Heating:Fuel | 275739.54 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 19887.1 | 2.83 | 9.67 | 10.23 | 10 | Coil:Heating:Fuel | 57228.96 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 21298.1 | 2.8 | 9.56 | 10.11 | 9.89 | Coil:Heating:Fuel | 58690.2 | Fan:VariableVolume | 0.75 | 640 | 0.89 | 755.59 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 95819.5 | 2.74 | 9.37 | 9.91 | 9.71 | Coil:Heating:Fuel | 275739.54 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 95819.5 | 2.69 | 9.19 | 9.73 | 9.54 | Coil:Heating:Fuel | 275739.54 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 21377.3 | 2.8 | 9.57 | 10.12 | 9.9 | Coil:Heating:Fuel | 58772.27 | Fan:VariableVolume | 0.75 | 640 | 0.89 | 758.41 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 26029.8 | 2.84 | 9.68 | 10.24 | 10.01 | Coil:Heating:Fuel | 70496 | Fan:VariableVolume | 0.75 | 640 | 1.08 | 923.46 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 8465.2 | 3.31 | 11.3 | 11.94 | 11.53 | Coil:Heating:Fuel | 21893.01 | Fan:VariableVolume | 0.75 | 640 | 0.35 | 300.32 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 95868.6 | 2.73 | 9.32 | 9.86 | 9.66 | Coil:Heating:Fuel | 234627.72 | Fan:VariableVolume | 0.75 | 640 | 3.99 | 3401.14 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 86546.8 | 2.75 | 9.39 | 9.93 | 9.71 | Coil:Heating:Fuel | 180667.57 | Fan:VariableVolume | 0.75 | 640 | 3.73 | 3179.28 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 33654.7 | 2.82 | 9.61 | 10.17 | 9.94 | Coil:Heating:Fuel | 66994.69 | Fan:VariableVolume | 0.75 | 640 | 1.4 | 1193.97 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 20784.4 | 2.81 | 9.57 | 10.13 | 9.91 | Coil:Heating:Fuel | 59811.29 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 20784.4 | 2.81 | 9.57 | 10.13 | 9.91 | Coil:Heating:Fuel | 59811.29 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 15786 | 2.79 | 9.51 | 10.06 | 9.79 | Coil:Heating:Fuel | 27623.29 | Fan:VariableVolume | 0.75 | 640 | 0.71 | 605.89 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 20684.3 | 2.78 | 9.48 | 10.02 | 9.69 | Coil:Heating:Fuel | 35083.74 | Fan:VariableVolume | 0.75 | 640 | 1.01 | 861.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 10878.1 | 3.26 | 11.14 | 11.76 | 11.28 | Coil:Heating:Fuel | 18153.91 | Fan:VariableVolume | 0.75 | 640 | 0.5 | 427.61 | 853.33 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 99181.5 | 2.75 | 9.38 | 9.92 | 9.67 | Coil:Heating:Fuel | 176715.25 | Fan:VariableVolume | 0.75 | 640 | 4.45 | 3794.37 | 853.33 | 6
Baseboard:Convective:Water for each zone
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 0.000428 | 873.52
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 0.00018 | 366.75
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 0.000552 | 1126.27
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 0.000553 | 1126.83
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 0.00018 | 366.46
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 0.000211 | 430.24
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 0.000704 | 1436.02
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 0.000703 | 1434.95
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 0.000211 | 430.7
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 0.000184 | 374.44
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 3.6e-05 | 73.8
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 0.000537 | 1082.31
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 0.000623 | 1259.58
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 0.000299 | 610.8
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 6.7e-05 | 136.3
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 8.5e-05 | 174
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 0.000193 | 393.81
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 0.000245 | 500.65
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 8.3e-05 | 168.71
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 0.000103 | 209.32
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 0.000284 | 578.85
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 0.000315 | 643.46
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 0.000401 | 818.48
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 0.000442 | 902.12
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 7.5e-05 | 152.66
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 0.000116 | 237.96
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 443926.3 | 0.339 | 0.2386 | NA | NA | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
26 DOAS systems with sensible & latent heat recover (erv) - one for each zone (26)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.214 | 26.5327
roof | 0.142 | 39.9859
window | 1.901 | 2.9868
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 11796.3 | 3.17 | 10.82 | 11.42 | 10.8 | Coil:Heating:Fuel | 20715.28 | Fan:VariableVolume | 0.75 | 640 | 0.65 | 555.23 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 149853 | 2.72 | 9.29 | 9.81 | 9.37 | Coil:Heating:Fuel | 261995.81 | Fan:VariableVolume | 0.75 | 640 | 8.69 | 7413.72 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 68765.8 | 2.53 | 8.65 | 9.14 | 8.78 | Coil:Heating:Fuel | 118808.16 | Fan:VariableVolume | 0.75 | 640 | 4.01 | 3420.02 | 853.33 | 1
Baseboard:Convective:Water for each zone
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
1 | 0.000156 | 318.39
2 | 0.002459 | 5021.96
3 | 0.000856 | 1747.85
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 5451.3 | 0.918 | 0.8307 | NA | NA | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.06 | 2207.44 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.264 | 21.5076
roof | 0.153 | 37.1111
window | 1.901 | 2.9868
lighting

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 91512.8 | 2.72 | 9.27 | 9.81 | 9.62 | Coil:Heating:Fuel | 179286.11 | Fan:VariableVolume | 0.75 | 640 | 3.8 | 3246.61 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 19917.7 | 2.67 | 9.11 | 9.62 | 9.16 | Coil:Heating:Fuel | 40077.09 | Fan:VariableVolume | 0.75 | 640 | 1.21 | 1034.68 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 36164.4 | 2.72 | 9.28 | 9.81 | 9.46 | Coil:Heating:Fuel | 67007.14 | Fan:VariableVolume | 0.75 | 640 | 1.87 | 1592.27 | 853.33 | 1
Baseboard:Convective:Water for each zone
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
1 | 0.000991 | 2023.2
2 | 0.000184 | 376.63
3 | 0.000282 | 576.69
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2645.2 | 1.093 | 1.0487 | NA | NA | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0.01 | 357.06 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.264 | 21.5076
roof | 0.153 | 37.1111
window | 1.901 | 2.9868
lighting