## school
Secondary School
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 72574 | 2.52 | 8.6 | 9.09 | 8.76 | Coil:Heating:Fuel | 341130.13 | Fan:VariableVolume | 0.7 | 640 | 4.07 | 3716.96 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 15591.1 | 2.72 | 9.3 | 9.82 | 9.45 | Coil:Heating:Fuel | 69376.94 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 71616.7 | 2.51 | 8.58 | 9.07 | 8.75 | Coil:Heating:Fuel | 334270.7 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 78111.2 | 2.58 | 8.8 | 9.31 | 9.02 | Coil:Heating:Fuel | 334270.7 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 15591.1 | 2.72 | 9.27 | 9.79 | 9.43 | Coil:Heating:Fuel | 69376.94 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 15591.1 | 2.73 | 9.31 | 9.83 | 9.46 | Coil:Heating:Fuel | 69376.94 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 78111.2 | 2.63 | 8.97 | 9.48 | 9.18 | Coil:Heating:Fuel | 334270.7 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 71616.7 | 2.53 | 8.65 | 9.14 | 8.81 | Coil:Heating:Fuel | 334270.7 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 15591.1 | 2.74 | 9.33 | 9.86 | 9.49 | Coil:Heating:Fuel | 69376.94 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 17542.2 | 2.7 | 9.22 | 9.74 | 9.33 | Coil:Heating:Fuel | 82456.41 | Fan:VariableVolume | 0.7 | 640 | 0.98 | 898.45 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 5623.9 | 3.2 | 10.91 | 11.51 | 10.92 | Coil:Heating:Fuel | 24859.69 | Fan:VariableVolume | 0.7 | 640 | 0.3 | 270.87 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 57164.4 | 2.58 | 8.79 | 9.29 | 8.99 | Coil:Heating:Fuel | 252688.98 | Fan:VariableVolume | 0.7 | 640 | 3.01 | 2753.3 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 44031.5 | 2.57 | 8.75 | 9.24 | 8.8 | Coil:Heating:Fuel | 180607.51 | Fan:VariableVolume | 0.7 | 640 | 2.79 | 2551.77 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 12124.2 | 2.7 | 9.21 | 9.72 | 9.26 | Coil:Heating:Fuel | 60870.42 | Fan:VariableVolume | 0.7 | 640 | 0.73 | 663.24 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 16943.3 | 3.21 | 10.96 | 11.57 | 11.01 | Coil:Heating:Fuel | 72507.42 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 16943.3 | 3.21 | 10.96 | 11.57 | 11.01 | Coil:Heating:Fuel | 72507.42 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 7636.6 | 2.69 | 9.19 | 9.71 | 9.29 | Coil:Heating:Fuel | 23839.42 | Fan:VariableVolume | 0.7 | 640 | 0.44 | 399.25 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 9604.8 | 2.69 | 9.18 | 9.69 | 9.23 | Coil:Heating:Fuel | 27282.84 | Fan:VariableVolume | 0.7 | 640 | 0.58 | 532.32 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 4722.6 | 3.17 | 10.83 | 11.43 | 10.81 | Coil:Heating:Fuel | 13831.59 | Fan:VariableVolume | 0.7 | 640 | 0.26 | 237.02 | 914.29 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 44192.6 | 2.6 | 8.87 | 9.37 | 8.98 | Coil:Heating:Fuel | 150685.38 | Fan:VariableVolume | 0.7 | 640 | 2.58 | 2359.82 | 914.29 | 6
Baseboard:Convective:Water for each zone |  |  |  | Hot water Boiler
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 0.00035 | 704.77 |  | Gas | 295504.19 | 0.004397 | 0.96
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 6.3e-05 | 126.13 |  | Hot water pump
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 0.000148 | 298.06 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 0.000148 | 296.19 |  | Pump:VariableSpeed | Intermittent | 179352 | 0.004397 | 1323.19 | 300960.01 | 0.9
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 6.3e-05 | 126.7 |  | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 0.000125 | 251.33
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 0.00041 | 826.5
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 0.000412 | 829.75
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 0.000124 | 250.97
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 5.1e-05 | 101.96
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 1.6e-05 | 32.85
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 0.000523 | 1051.43
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 0.000477 | 960.63
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 0.000199 | 402.44
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 2.4e-05 | 49.6
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 5.5e-05 | 110.68
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 5.9e-05 | 118.34
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 0.00013 | 261.42
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 2.7e-05 | 55.89
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 6.6e-05 | 132.55
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 0.00012 | 243.13
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 0.000126 | 257.21
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 0.000256 | 518.32
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 0.000302 | 610.3
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 4e-05 | 81.01
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 8.1e-05 | 164.17
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 355166 | 1.001 | 0.6506 | 0.019919 | 22.35 | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
26 DOAS systems with sensible & latent heat recover (erv) - one for each zone (26)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 4480.6 | 3.1 | 10.57 | 11.13 | 10.42 | Coil:Heating:Fuel | 12763.26 | Fan:VariableVolume | 0.7 | 640 | 0.28 | 258.23 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 70339.5 | 2.63 | 8.98 | 9.48 | 9 | Coil:Heating:Fuel | 166628.6 | Fan:VariableVolume | 0.7 | 640 | 4.46 | 4076.41 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 25633 | 2.49 | 8.49 | 8.96 | 8.56 | Coil:Heating:Fuel | 64113.99 | Fan:VariableVolume | 0.7 | 640 | 1.62 | 1485.52 | 914.29 | 1
Baseboard:Convective:Water for each zone
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  |  | Hot water Boiler
1 | 8e-05 | 146.14 |  |  | Fuel | Design Size Nominal Capacity [W] | Design Size Design Water Flow Rate | Thermal efficiency
2 | 0.001653 | 2739.84 |  |  | Gas | 156075.23 | 0.002322 | 0.96
3 | 0.000589 | 1187.95 |  |  | Gas | 156075.23 | 0.002322 | 0.96
Hot water pump
[5 empty] | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
[5 empty] | Pump:VariableSpeed | Intermittent | 179352 | 0.002322 | 698.87 | 300960 | 0.86
[5 empty] | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 4376.2 | 13.22 | 1.7806 | 0.000245 | 0.27448 | 0.000245
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 39078.3 | 2.61 | 8.9 | 9.41 | 9.12 | Coil:Heating:Fuel | 157525.65 | Fan:VariableVolume | 0.7 | 640 | 1.99 | 1822.17 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 8369.7 | 2.65 | 9.03 | 9.53 | 9.05 | Coil:Heating:Fuel | 24835.75 | Fan:VariableVolume | 0.7 | 640 | 0.53 | 485.05 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 9968.3 | 2.67 | 9.09 | 9.6 | 9.11 | Coil:Heating:Fuel | 39487.91 | Fan:VariableVolume | 0.7 | 640 | 0.63 | 577.69 | 914.29 | 1
Baseboard:Convective:Water for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | Design Size Nominal Capacity [W] | Design Size Design Water Flow Rate | Thermal efficiency
1 | 0.000728 | 1469.67 |  | Gas | 68617.13 | 0.001021 | 0.96
2 | 0.000113 | 228.1 |  | Hot water pump
3 | 0.000179 | 361.77 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
|  |  |  | Pump:VariableSpeed | Intermittent | 179352 | 0.001021 | 307.25 | 300960 | 0.85
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2131.3 | 9.86 | 1.983 | 0.000119 | 0.13319 | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0 | 274.66 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## highrise
Highrise
3 central DOAS units (with heating & cooling)
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Design Size Rated Capacity [W] | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat ( in total)
1 | Coil:Cooling:DX:SingleSpeed | 43581 | 2.64 | 9.01 | 9.51 | 9.03 | Coil:Heating:Water | 231797.12 | 0.003462 | 3734.75 | Fan:VariableVolume | 0.82 | 640 | 2.76 | 2156.05 | 780.49 | 79
2 | Coil:Cooling:DX:SingleSpeed | 3734.3 | 2.65 | 9.03 | 9.53 | 9.05 | Coil:Heating:Fuel | 19861.78 | N/A | N/A | Fan:VariableVolume | 0.82 | 640 | 0.24 | 184.74 | 780.49 | 10
3 (different from previous systems) | Coil:Cooling:Water | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Sensible Heat Ratio | Nominal Coil UA Value [W/C] | Nominal Coil Surface Area [m2] | Coil:Heating:Water | 566.21 | 8e-06 | 7.05 | Fan:VariableVolume | 0.82 | 250 | 0.04 | 11.34 | 304.88 | 1 | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
|  | 773.24 | 536.7 | 236.54 | 0.69 | 77.28 |  |  |  |  | Fan:VariableVolume | 0.82 | 1000 | 0.04 | 45.38 | 1219.51 |  | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
Hot water baseboard for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 1.1e-05 | 18.65 |  | Gas | 497824.25 | 0.003908 | 96%
2 | 1e-05 | 18.81 |  | Hot water pump
3 | 1.8e-05 | 32.81 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
4 | 1.3e-05 | 23.65 |  | Pump:VariableSpeed | Intermittent | 179352 | 0.003908 | 1176.04 | 300960.01 | 0.9
5 | 1.3e-05 | 23.2
6 | 1.8e-05 | 32.81
7 | 0 | 0
8 | 1.3e-05 | 23.65
9 | 1.8e-05 | 32.92
10 | 7e-06 | 14.79
11 | 7e-06 | 14.7
12 | 3e-06 | 6.66
13 | 3e-06 | 6.6
14 | 7e-06 | 14.79
15 | 3e-06 | 6.66
16 | 3e-06 | 6.81
17 | 2e-06 | 3.59
18 | 2e-06 | 3.62
19 | 6e-06 | 11.44
20 | 2e-06 | 3.53
21 | 6e-06 | 11.44
22 | 2e-06 | 3.59
23 | 6e-06 | 11.36
24 | 6e-06 | 12.54
25 | 5e-06 | 10.42
26 | 1e-06 | 2.62
27 | 1e-06 | 2.59
28 | 5e-06 | 10.65
29 | 5e-06 | 10.5
30 | 5e-06 | 10.5
31 | 1e-06 | 2.64
32 | 1e-06 | 2.64
33 | 5e-06 | 10.35
34 | 5e-06 | 10.38
35 | 5e-06 | 10.3
36 | 1e-06 | 2.35
37 | 5e-06 | 10.38
38 | 1e-06 | 2.4
39 | 1e-06 | 2.34
40 | 1e-06 | 2.4
41 | 5e-06 | 10.44
42 | 1e-06 | 2.42
43 | 5e-06 | 10.49
44 | 1e-06 | 2.42
45 | 1e-06 | 2.36
46 | 1e-06 | 2.35
47 | 5e-06 | 10.49
48 | 5e-06 | 10.41
49 | 5e-06 | 10.73
50 | 1e-06 | 2.59
51 | 5e-06 | 10.73
52 | 1e-06 | 2.59
53 | 5e-06 | 10.67
54 | 5e-06 | 10.58
55 | 1e-06 | 2.51
56 | 1e-06 | 2.53
57 | 1e-06 | 2.99
58 | 6e-06 | 11.18
59 | 1e-06 | 2.84
60 | 6e-06 | 11.18
61 | 5e-06 | 10.73
62 | 5e-06 | 11.12
63 | 1e-06 | 2.99
64 | 1e-06 | 2.92
65 | 2e-06 | 3.91
66 | 6e-06 | 12.32
67 | 2e-06 | 3.65
68 | 2e-06 | 4
69 | 6e-06 | 12.32
70 | 6e-06 | 12.28
71 | 5e-06 | 10.58
72 | 2e-06 | 4
73 | 4e-06 | 7.38
74 | 8e-06 | 16.88
75 | 4e-06 | 7.21
76 | 4e-06 | 9.03
77 | 8e-06 | 16.88
78 | 3e-06 | 6.07
79 | 4e-06 | 7.38
80 | 8e-06 | 16.86
81 | 1.7e-05 | 31.45
82 | 7e-06 | 13.61
83 | 4e-06 | 8.51
84 | 3e-06 | 6.84
85 | 3e-06 | 6.43
86 | 3e-06 | 6.41
87 | 3e-06 | 6.58
88 | 3e-06 | 7.01
89 | 4e-06 | 8.11
90 | 6e-06 | 12.26
Chilled water loop
Chiller type | Nominal Capacity [W] | Nominal Efficiency [W/W] | IPLV in SI Units [W/W | Design Size Reference Chilled Water Flow Rate [m3/s | Design Size Reference Condenser Fluid Flow Rate [m3/s]
CHILLER WATERCOOLED SCROLL | 5600.28 | 4.5 | 5.61 | 2.5e-05 | 0.000273
CHILLER WATERCOOLED SCROLL
cooling tower type | Nominal Capacity [W] | Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | U-Factor Times Area Value at Design Air Flow Rate [W/C] | Free Convection Regime Air Flow Rate [m3/s] | Free Convection U-Factor Times Area Value [W/K]
CoolingTower:SingleSpeed | 4562.51 | 0.000273 | 0.25528 | 237.21 | 0.025528 | 23.72
air cooled variable refrigerant flow (VRF) system with a single outdoor and multiple indoor units
vrf component | Design Size Rated Total Cooling Capacity (gross) [W] | Design Size Rated Total Heating Capacity [W] | Design Size Resistive Defrost Heater Capacity | User-Specified Resistive Defrost Heater Capacity | Design Size Evaporative Condenser Air Flow Rate [m3/s] | Design Size Evaporative Condenser Pump Rated Power Consumption [W]
outdoor unit | 105534.19 | 105534.19 | 105534.19 | 0 | 12.03 | 450.21
terminal units (indoor) largest size shown | Design Size Cooling Supply Air Flow Rate [m3/s] | Design Size Heating Supply Air Flow Rate [m3/s]
indoor unit x 90 (largest size shown) | 0.18555 | 0.18555
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate
Air source heat pump water heater with back up electrical heating element | 2.6667 | 111497 | 0.751 | 0.8678 | 0.006252 | 7.02 | 0.000743
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 580545.91 | 0.000743 | 646.5 | 870514.18 | 0.85
3 sensible & latent heat recover (erv) in total - one for each air loop
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.2367 | 0.2367 | 90% | 200
0.037209 | 0.037209
2.76 | 2.76
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.06 | 94.6333 | 3392.42 |  | No
roof | 0.057 | 99.614 | 783.65
window | 0.7 | 8.1114 | 462.6
floor |  |  | 7836.5
Stories |  |  |  | 10
lighting
50% reduction
Packaged terminal air conditioner (heat & cool; use cooling coil flow as design flowrate
Coil Type | Coil Final Gross Total Capacity [W] | Coil Final Reference Air Volume Flow Rate [m3/s]
COIL:COOLING:DX:SINGLESPEED | 1141.264 | 0.067052
COIL:HEATING:ELECTRIC | 681.111 | -999
COIL:COOLING:DX:SINGLESPEED | 1740.596 | 0.10515
COIL:HEATING:ELECTRIC | 1189.948 | -999
COIL:COOLING:DX:SINGLESPEED | 956.146 | 0.057761
COIL:HEATING:ELECTRIC | 856.869 | -999
COIL:COOLING:DX:SINGLESPEED | 1148.462 | 0.067732
COIL:HEATING:ELECTRIC | 840.486 | -999
COIL:COOLING:DX:SINGLESPEED | 1926.588 | 0.11639
COIL:HEATING:ELECTRIC | 1189.948 | -999
COIL:COOLING:DX:SINGLESPEED | 3071.497 | 0.18555
COIL:HEATING:ELECTRIC | 0 | -999
COIL:COOLING:DX:SINGLESPEED | 993.61 | 0.060024
COIL:HEATING:ELECTRIC | 856.868 | -999
COIL:COOLING:DX:SINGLESPEED | 1726.534 | 0.1043
COIL:HEATING:ELECTRIC | 1193.863 | -999
COIL:COOLING:DX:SINGLESPEED | 1294.805 | 0.078219
COIL:HEATING:ELECTRIC | 488.457 | -999
COIL:COOLING:DX:SINGLESPEED | 1576.027 | 0.095208
COIL:HEATING:ELECTRIC | 485.418 | -999
COIL:COOLING:DX:SINGLESPEED | 732.37 | 0.044242
COIL:HEATING:ELECTRIC | 220.004 | -999
COIL:COOLING:DX:SINGLESPEED | 721.926 | 0.043612
COIL:HEATING:ELECTRIC | 218.267 | -999
COIL:COOLING:DX:SINGLESPEED | 1523.311 | 0.092023
COIL:HEATING:ELECTRIC | 488.457 | -999
COIL:COOLING:DX:SINGLESPEED | 710.743 | 0.042936
COIL:HEATING:ELECTRIC | 220.004 | -999
COIL:COOLING:DX:SINGLESPEED | 704.836 | 0.042579
COIL:HEATING:ELECTRIC | 225.637 | -999
COIL:COOLING:DX:SINGLESPEED | 831.101 | 0.050207
COIL:HEATING:ELECTRIC | 118.838 | -999
COIL:COOLING:DX:SINGLESPEED | 846.986 | 0.051166
COIL:HEATING:ELECTRIC | 119.982 | -999
COIL:COOLING:DX:SINGLESPEED | 1570.288 | 0.094861
COIL:HEATING:ELECTRIC | 378.234 | -999
COIL:COOLING:DX:SINGLESPEED | 861.245 | 0.052028
COIL:HEATING:ELECTRIC | 116.988 | -999
COIL:COOLING:DX:SINGLESPEED | 1305.453 | 0.078862
COIL:HEATING:ELECTRIC | 378.234 | -999
COIL:COOLING:DX:SINGLESPEED | 847.66 | 0.051207
COIL:HEATING:ELECTRIC | 118.838 | -999
COIL:COOLING:DX:SINGLESPEED | 1644.924 | 0.09937
COIL:HEATING:ELECTRIC | 375.52 | -999
COIL:COOLING:DX:SINGLESPEED | 1337.84 | 0.080819
COIL:HEATING:ELECTRIC | 414.396 | -999
COIL:COOLING:DX:SINGLESPEED | 1670.645 | 0.10092
COIL:HEATING:ELECTRIC | 344.733 | -999
COIL:COOLING:DX:SINGLESPEED | 871.813 | 0.052666
COIL:HEATING:ELECTRIC | 86.884 | -999
COIL:COOLING:DX:SINGLESPEED | 888.268 | 0.05366
COIL:HEATING:ELECTRIC | 85.705 | -999
COIL:COOLING:DX:SINGLESPEED | 1342.401 | 0.081094
COIL:HEATING:ELECTRIC | 352.297 | -999
COIL:COOLING:DX:SINGLESPEED | 1598.184 | 0.096546
COIL:HEATING:ELECTRIC | 347.16 | -999
COIL:COOLING:DX:SINGLESPEED | 1338.349 | 0.08085
COIL:HEATING:ELECTRIC | 347.16 | -999
COIL:COOLING:DX:SINGLESPEED | 877.24 | 0.052994
COIL:HEATING:ELECTRIC | 87.657 | -999
COIL:COOLING:DX:SINGLESPEED | 860.915 | 0.052008
COIL:HEATING:ELECTRIC | 87.657 | -999
COIL:COOLING:DX:SINGLESPEED | 1344.061 | 0.081195
COIL:HEATING:ELECTRIC | 342.244 | -999
COIL:COOLING:DX:SINGLESPEED | 1345.135 | 0.08126
COIL:HEATING:ELECTRIC | 343.115 | -999
COIL:COOLING:DX:SINGLESPEED | 1676.917 | 0.1013
COIL:HEATING:ELECTRIC | 340.672 | -999
COIL:COOLING:DX:SINGLESPEED | 876.773 | 0.052966
COIL:HEATING:ELECTRIC | 77.953 | -999
COIL:COOLING:DX:SINGLESPEED | 1604.917 | 0.096953
COIL:HEATING:ELECTRIC | 343.115 | -999
COIL:COOLING:DX:SINGLESPEED | 883.64 | 0.053381
COIL:HEATING:ELECTRIC | 79.584 | -999
COIL:COOLING:DX:SINGLESPEED | 893.906 | 0.054001
COIL:HEATING:ELECTRIC | 77.54 | -999
COIL:COOLING:DX:SINGLESPEED | 867.231 | 0.052389
COIL:HEATING:ELECTRIC | 79.584 | -999
COIL:COOLING:DX:SINGLESPEED | 1343.633 | 0.081169
COIL:HEATING:ELECTRIC | 345.137 | -999
COIL:COOLING:DX:SINGLESPEED | 884.801 | 0.053451
COIL:HEATING:ELECTRIC | 80.286 | -999
COIL:COOLING:DX:SINGLESPEED | 1345.79 | 0.081299
COIL:HEATING:ELECTRIC | 346.977 | -999
COIL:COOLING:DX:SINGLESPEED | 868.375 | 0.052459
COIL:HEATING:ELECTRIC | 80.286 | -999
COIL:COOLING:DX:SINGLESPEED | 877.507 | 0.05301
COIL:HEATING:ELECTRIC | 78.384 | -999
COIL:COOLING:DX:SINGLESPEED | 894.784 | 0.054054
COIL:HEATING:ELECTRIC | 78.027 | -999
COIL:COOLING:DX:SINGLESPEED | 1605.911 | 0.097013
COIL:HEATING:ELECTRIC | 346.977 | -999
COIL:COOLING:DX:SINGLESPEED | 1677.709 | 0.10135
COIL:HEATING:ELECTRIC | 344.037 | -999
COIL:COOLING:DX:SINGLESPEED | 1605.779 | 0.097005
COIL:HEATING:ELECTRIC | 354.793 | -999
COIL:COOLING:DX:SINGLESPEED | 868.452 | 0.052463
COIL:HEATING:ELECTRIC | 85.984 | -999
COIL:COOLING:DX:SINGLESPEED | 1345.395 | 0.081275
COIL:HEATING:ELECTRIC | 354.793 | -999
COIL:COOLING:DX:SINGLESPEED | 884.88 | 0.053456
COIL:HEATING:ELECTRIC | 85.984 | -999
COIL:COOLING:DX:SINGLESPEED | 1342.92 | 0.081126
COIL:HEATING:ELECTRIC | 352.782 | -999
COIL:COOLING:DX:SINGLESPEED | 1677.411 | 0.10133
COIL:HEATING:ELECTRIC | 349.597 | -999
COIL:COOLING:DX:SINGLESPEED | 894.672 | 0.054047
COIL:HEATING:ELECTRIC | 83.05 | -999
COIL:COOLING:DX:SINGLESPEED | 877.366 | 0.053002
COIL:HEATING:ELECTRIC | 83.907 | -999
COIL:COOLING:DX:SINGLESPEED | 868.477 | 0.052465
COIL:HEATING:ELECTRIC | 99.057 | -999
COIL:COOLING:DX:SINGLESPEED | 1605.427 | 0.096984
COIL:HEATING:ELECTRIC | 369.367 | -999
COIL:COOLING:DX:SINGLESPEED | 894.469 | 0.054035
COIL:HEATING:ELECTRIC | 94.047 | -999
COIL:COOLING:DX:SINGLESPEED | 1344.918 | 0.081247
COIL:HEATING:ELECTRIC | 369.367 | -999
COIL:COOLING:DX:SINGLESPEED | 1676.857 | 0.1013
COIL:HEATING:ELECTRIC | 354.66 | -999
COIL:COOLING:DX:SINGLESPEED | 1342.226 | 0.081084
COIL:HEATING:ELECTRIC | 367.408 | -999
COIL:COOLING:DX:SINGLESPEED | 884.895 | 0.053457
COIL:HEATING:ELECTRIC | 99.057 | -999
COIL:COOLING:DX:SINGLESPEED | 877.17 | 0.05299
COIL:HEATING:ELECTRIC | 96.694 | -999
COIL:COOLING:DX:SINGLESPEED | 878.787 | 0.053088
COIL:HEATING:ELECTRIC | 129.312 | -999
COIL:COOLING:DX:SINGLESPEED | 1606.128 | 0.097026
COIL:HEATING:ELECTRIC | 407.019 | -999
COIL:COOLING:DX:SINGLESPEED | 895.997 | 0.054127
COIL:HEATING:ELECTRIC | 120.823 | -999
COIL:COOLING:DX:SINGLESPEED | 886.717 | 0.053567
COIL:HEATING:ELECTRIC | 132.259 | -999
COIL:COOLING:DX:SINGLESPEED | 1343.169 | 0.081141
COIL:HEATING:ELECTRIC | 407.019 | -999
COIL:COOLING:DX:SINGLESPEED | 1339.861 | 0.080941
COIL:HEATING:ELECTRIC | 405.396 | -999
COIL:COOLING:DX:SINGLESPEED | 1677.309 | 0.10133
COIL:HEATING:ELECTRIC | 349.579 | -999
COIL:COOLING:DX:SINGLESPEED | 870.381 | 0.05258
COIL:HEATING:ELECTRIC | 132.259 | -999
COIL:COOLING:DX:SINGLESPEED | 890.727 | 0.053809
COIL:HEATING:ELECTRIC | 244.532 | -999
COIL:COOLING:DX:SINGLESPEED | 1337.792 | 0.080816
COIL:HEATING:ELECTRIC | 556.603 | -999
COIL:COOLING:DX:SINGLESPEED | 898.244 | 0.054263
COIL:HEATING:ELECTRIC | 238.781 | -999
COIL:COOLING:DX:SINGLESPEED | 1709.572 | 0.10328
COIL:HEATING:ELECTRIC | 297.584 | -999
COIL:COOLING:DX:SINGLESPEED | 1637.487 | 0.098921
COIL:HEATING:ELECTRIC | 556.603 | -999
COIL:COOLING:DX:SINGLESPEED | 916.668 | 0.055376
COIL:HEATING:ELECTRIC | 200.988 | -999
COIL:COOLING:DX:SINGLESPEED | 908.304 | 0.054871
COIL:HEATING:ELECTRIC | 244.532 | -999
COIL:COOLING:DX:SINGLESPEED | 1330.624 | 0.080383
COIL:HEATING:ELECTRIC | 556.185 | -999