## school
Secondary School
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 68347.6 | 2.49 | 8.5 | 8.98 | 8.62 | Coil:Heating:Fuel | 372897.07 | Fan:VariableVolume | 0.7 | 640 | 4.07 | 3716.96 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 14769.9 | 2.7 | 9.2 | 9.72 | 9.32 | Coil:Heating:Fuel | 75837.5 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 67498.6 | 2.49 | 8.48 | 8.97 | 8.62 | Coil:Heating:Fuel | 365398.87 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 74290.5 | 2.54 | 8.67 | 9.17 | 8.87 | Coil:Heating:Fuel | 365398.87 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 14769.9 | 3.16 | 10.8 | 11.39 | 10.76 | Coil:Heating:Fuel | 75837.5 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 14769.9 | 2.7 | 9.2 | 9.72 | 9.32 | Coil:Heating:Fuel | 75837.5 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 74290.5 | 2.59 | 8.83 | 9.33 | 9.01 | Coil:Heating:Fuel | 365398.87 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 67498.6 | 2.5 | 8.52 | 9 | 8.65 | Coil:Heating:Fuel | 365398.87 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 14769.9 | 2.7 | 9.23 | 9.75 | 9.34 | Coil:Heating:Fuel | 75837.5 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 16520.7 | 2.67 | 9.11 | 9.62 | 9.19 | Coil:Heating:Fuel | 90134.97 | Fan:VariableVolume | 0.7 | 640 | 0.98 | 898.45 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 5331.3 | 3.17 | 10.81 | 11.4 | 10.78 | Coil:Heating:Fuel | 27174.69 | Fan:VariableVolume | 0.7 | 640 | 0.3 | 270.87 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 54190.6 | 2.54 | 8.68 | 9.17 | 8.84 | Coil:Heating:Fuel | 276220.06 | Fan:VariableVolume | 0.7 | 640 | 3.01 | 2753.3 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 44739.9 | 2.52 | 8.61 | 9.09 | 8.67 | Coil:Heating:Fuel | 197490.16 | Fan:VariableVolume | 0.7 | 640 | 2.84 | 2592.83 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 11444.5 | 2.66 | 9.08 | 9.58 | 9.1 | Coil:Heating:Fuel | 66538.84 | Fan:VariableVolume | 0.7 | 640 | 0.73 | 663.24 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 16114.5 | 3.19 | 10.87 | 11.47 | 10.88 | Coil:Heating:Fuel | 79259.5 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 16114.5 | 3.19 | 10.87 | 11.47 | 10.88 | Coil:Heating:Fuel | 79259.5 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 7720.8 | 2.68 | 9.14 | 9.66 | 9.23 | Coil:Heating:Fuel | 26178.05 | Fan:VariableVolume | 0.7 | 640 | 0.45 | 412.84 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 9559.1 | 2.67 | 9.11 | 9.61 | 9.13 | Coil:Heating:Fuel | 29781.9 | Fan:VariableVolume | 0.7 | 640 | 0.6 | 546.39 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 4550 | 3.16 | 10.79 | 11.38 | 10.74 | Coil:Heating:Fuel | 14882.64 | Fan:VariableVolume | 0.7 | 640 | 0.26 | 233.92 | 914.29 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 42075.5 | 2.56 | 8.72 | 9.21 | 8.81 | Coil:Heating:Fuel | 162683.11 | Fan:VariableVolume | 0.7 | 640 | 2.55 | 2331.83 | 914.29 | 6
Baseboard:Convective:Water for each zone
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 0.000359 | 722.75
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 6.8e-05 | 136.42
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 0.000154 | 309.84
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 0.000154 | 308.86
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 6.8e-05 | 137.12
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 0.000128 | 258.19
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 0.000425 | 855.64
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 0.000427 | 859.46
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 0.000128 | 257.72
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 5.6e-05 | 113.21
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 1.8e-05 | 35.68
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 0.000534 | 1073.75
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 0.000489 | 983.81
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 0.000206 | 414.52
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 2.6e-05 | 51.97
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 5.7e-05 | 114.19
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 5.5e-05 | 109.95
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 0.000134 | 269.12
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 2.9e-05 | 58.17
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 6.7e-05 | 135.87
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 0.000124 | 251.59
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 0.000132 | 268.36
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 0.000262 | 528.67
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 0.000312 | 630.39
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 4.1e-05 | 83.8
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 8.3e-05 | 167.23
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 359113.9 | 1.009 | 0.6557 | 0.019919 | 22.35 | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
26 DOAS systems with sensible & latent heat recover (erv) - one for each zone (26)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 4436.6 | 3.09 | 10.56 | 11.13 | 10.41 | Coil:Heating:Fuel | 13611.84 | Fan:VariableVolume | 0.7 | 640 | 0.28 | 256.54 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 63060.6 | 2.58 | 8.79 | 9.28 | 8.83 | Coil:Heating:Fuel | 165081.2 | Fan:VariableVolume | 0.7 | 640 | 4 | 3654.58 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 22218.7 | 2.47 | 8.41 | 8.89 | 8.49 | Coil:Heating:Fuel | 63024.42 | Fan:VariableVolume | 0.7 | 640 | 1.41 | 1287.65 | 914.29 | 1
Baseboard:Convective:Water for each zone
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
1 | 9.2e-05 | 187.15
2 | 0.001546 | 3153.27
3 | 0.000426 | 869.21
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 4425.2 | 2.664 | 2.264 | 0.000245 | 0.27448 | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 33561.6 | 2.56 | 8.74 | 9.24 | 8.92 | Coil:Heating:Fuel | 168015.19 | Fan:VariableVolume | 0.7 | 640 | 1.83 | 1674.74 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 10285.6 | 2.64 | 9.01 | 9.51 | 9.03 | Coil:Heating:Fuel | 29657.07 | Fan:VariableVolume | 0.7 | 640 | 0.65 | 596.08 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 9621.2 | 2.65 | 9.06 | 9.56 | 9.08 | Coil:Heating:Fuel | 42316.19 | Fan:VariableVolume | 0.7 | 640 | 0.61 | 557.58 | 914.29 | 1
Baseboard:Convective:Water for each zone
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K]
1 | 0.000571 | 1164
2 | 8.7e-05 | 176.87
3 | 0.000138 | 280.65
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2154.5 | 3.055 | 2.8151 | 0.000119 | 0.13319 | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0 | 274.66 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.06 | 94.6333
roof | 0.057 | 99.614
window | 0.7 | 8.1114
lighting

## highrise
Highrise
3 central DOAS units (with heating & cooling)
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat ( in total)
1 | Coil:Cooling:DX:SingleSpeed | 43581 | 2.68 | 9.16 | 9.67 | 9.17 | Coil:Heating:Electric | 156758.1 | Fan:VariableVolume | 0.6 | 640 | 0.24 | 252.48 | 1066.67 | 79
2 | Coil:Cooling:DX:SingleSpeed | 3734.3 | 2.69 | 9.17 | 9.68 | 9.18 | Coil:Heating:Electric | 13431.98 | Fan:VariableVolume | 0.6 | 640 | 0.24 | 252.48 | 1066.67 | 10
3 (different from previous systems; diff cooling coil type-->) | Coil:Cooling:Water | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Sensible Heat Ratio | Nominal Coil UA Value [W/C] | Nominal Coil Surface Area [m2] | Coil:Heating:Electric | 230.47 | There are 2 Fan:VariableVolume in this unit | 0.6 | 250 | 0.04 | 15.5 | 416.67 | 1 | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
|  | 813 | 596.51 | 0.73 | 95.03 | 0.96 |  |  |  | 0.6 | 1000 | 0.04 | 62.02 | 1666.67 |  | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
electric baseboard for each zone
No. | Design Size Heating Design Capacity [W]
1 | 858.6
2 | 1740.26
3 | 2386.85
4 | 1798.77
5 | 1780.38
6 | 2385.38
7 | 1711.72
8 | 1798.6
9 | 2373.74
10 | 742.68
11 | 730.42
12 | 380.19
13 | 368.92
14 | 742
15 | 380.26
16 | 371.69
17 | 288.83
18 | 281.19
19 | 681.83
20 | 279.38
21 | 682.55
22 | 288.78
23 | 670.42
24 | 706
25 | 670.08
26 | 268.19
27 | 267.33
28 | 676.71
29 | 681.36
30 | 681.94
31 | 276.84
32 | 276.89
33 | 690.45
34 | 700.96
35 | 688.98
36 | 273.13
37 | 700.23
38 | 282.3
39 | 272.89
40 | 282.36
41 | 711.46
42 | 292.58
43 | 722.58
44 | 292.64
45 | 283.47
46 | 283.35
47 | 721.85
48 | 710.54
49 | 744.19
50 | 305.29
51 | 744.9
52 | 305.24
53 | 734.36
54 | 733.38
55 | 296.18
56 | 296.31
57 | 329.05
58 | 772.55
59 | 317.68
60 | 773.27
61 | 760.2
62 | 762
63 | 328.99
64 | 318.02
65 | 371.69
66 | 829.84
67 | 370.62
68 | 382.18
69 | 830.57
70 | 819.06
71 | 812.6
72 | 382.25
73 | 595.17
74 | 1052.88
75 | 584.25
76 | 997.34
77 | 1052.05
78 | 578.82
79 | 595.09
80 | 1042.84
81 | 2509.52
82 | 574.18
83 | 442.58
84 | 409.48
85 | 408.15
86 | 416.08
87 | 427.83
88 | 447.75
89 | 499.37
90 | 738.87
Chilled water loop
Chiller type | Nominal Capacity [W] | Nominal Efficiency [W/W] | IPLV in SI Units [W/W | Design Size Reference Chilled Water Flow Rate [m3/s | Design Size Reference Condenser Fluid Flow Rate [m3/s]
CHILLER WATERCOOLED SCROLL | 5394.4 | 4.5 | 5.61 | 2.3e-05 | 0.000263
CHILLER WATERCOOLED SCROLL | 0 | 4.5 | 5.61 | 2.3e-05 | 0
cooling tower type | Nominal Capacity [W] | Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | U-Factor Times Area Value at Design Air Flow Rate [W/C] | Free Convection Regime Air Flow Rate [m3/s] | Free Convection U-Factor Times Area Value [W/K]
CoolingTower:SingleSpeed | 4394.79 | 0.000263 | 0.22605 | 249.4 | 0.022605 | 24.94
air cooled variable refrigerant flow (VRF) system with a single outdoor and multiple indoor units
vrf component | Design Size Rated Total Cooling Capacity (gross) [W] | Design Size Rated Total Heating Capacity [W] | Design Size Resistive Defrost Heater Capacity | User-Specified Resistive Defrost Heater Capacity | Design Size Evaporative Condenser Air Flow Rate [m3/s] | Design Size Evaporative Condenser Pump Rated Power Consumption [W]
outdoor unit | 152171.39 | 152171.39 | 152171.39 | 0 | 17.35 | 649.16
terminal units (indoor) largest size shown | Design Size Cooling Supply Air Flow Rate [m3/s] | Design Size Heating Supply Air Flow Rate [m3/s]
indoor unit x 90 (largest size shown) | 0.20206 | 0.20206
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.6667 | 113967.4 | 0.749 | 1.7184 | 0.006252 | 7.02 | 0.000743
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 580545.91 | 0.000743 | 646.5 | 870514.18 | 0.85
1 sensible & latent heat recover (erv)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
2.76 | 2.76 | 90% | 200
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.18 | 31.5444
roof | 0.142 | 39.9859
window | 1 | 5.678
lighting
70% reduction