## school
Secondary School
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 97785.8 | 2.71 | 9.24 | 9.78 | 9.59 | Coil:Heating:Electric | 323813.92 | Fan:VariableVolume | 0.75 | 640 | 4.07 | 3469.16 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 24311.1 | 2.88 | 9.84 | 10.41 | 10.16 | Coil:Heating:Electric | 70526.52 | Fan:VariableVolume | 0.75 | 640 | 1.01 | 862.49 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 95819.5 | 2.7 | 9.23 | 9.77 | 9.58 | Coil:Heating:Electric | 317302.68 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 95819.5 | 2.71 | 9.24 | 9.78 | 9.59 | Coil:Heating:Electric | 317302.68 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 24157.6 | 2.88 | 9.82 | 10.39 | 10.15 | Coil:Heating:Electric | 70364.49 | Fan:VariableVolume | 0.75 | 640 | 1 | 857.04 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 29681.5 | 2.89 | 9.87 | 10.44 | 10.19 | Coil:Heating:Electric | 76197.85 | Fan:VariableVolume | 0.75 | 640 | 1.23 | 1053.01 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 95819.5 | 2.8 | 9.55 | 10.1 | 9.89 | Coil:Heating:Electric | 317302.68 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 95819.5 | 2.73 | 9.32 | 9.86 | 9.66 | Coil:Heating:Electric | 317302.68 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 29783.4 | 2.85 | 9.71 | 10.27 | 10.04 | Coil:Heating:Electric | 76305.5 | Fan:VariableVolume | 0.75 | 640 | 1.24 | 1056.63 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 28482.7 | 2.88 | 9.83 | 10.4 | 10.16 | Coil:Heating:Electric | 83386.52 | Fan:VariableVolume | 0.75 | 640 | 1.18 | 1010.48 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 10422 | 3.25 | 11.1 | 11.72 | 11.23 | Coil:Heating:Electric | 28503.32 | Fan:VariableVolume | 0.75 | 640 | 0.49 | 417.69 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 96055.3 | 2.77 | 9.46 | 10.01 | 9.8 | Coil:Heating:Electric | 266573.78 | Fan:VariableVolume | 0.75 | 640 | 3.99 | 3407.76 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 122812.6 | 2.69 | 9.17 | 9.69 | 9.3 | Coil:Heating:Electric | 285955.2 | Fan:VariableVolume | 0.75 | 640 | 6.84 | 5840.97 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 33159.3 | 2.76 | 9.43 | 9.96 | 9.58 | Coil:Heating:Electric | 83401.06 | Fan:VariableVolume | 0.75 | 640 | 1.73 | 1479.82 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 20784.4 | 2.86 | 9.74 | 10.3 | 10.07 | Coil:Heating:Electric | 68826.84 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 20784.4 | 2.86 | 9.74 | 10.3 | 10.07 | Coil:Heating:Electric | 68826.84 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 14961.3 | 2.77 | 9.44 | 9.97 | 9.58 | Coil:Heating:Electric | 32428.92 | Fan:VariableVolume | 0.75 | 640 | 0.8 | 680.74 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 20714.3 | 2.78 | 9.48 | 10.02 | 9.61 | Coil:Heating:Electric | 40584.92 | Fan:VariableVolume | 0.75 | 640 | 1.12 | 954.68 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 10800.3 | 3.21 | 10.97 | 11.58 | 11.02 | Coil:Heating:Electric | 20891.55 | Fan:VariableVolume | 0.75 | 640 | 0.55 | 468.58 | 853.33 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 103689.1 | 2.73 | 9.3 | 9.83 | 9.48 | Coil:Heating:Electric | 216215.69 | Fan:VariableVolume | 0.75 | 640 | 5.33 | 4551.09 | 853.33 | 6
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
Design Size Heating Design Capacity [W]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 32890.19
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 13408.99
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 41062.13
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 41137.92
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 13386.86
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 16110.3
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 54079.33
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 53987.99
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 16138.24
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 14165.97
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 3017.23
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 41259.35
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 47975.44
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 23555.86
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 5029.99
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 6615.05
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 14571.63
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 18901.4
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 6087.89
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 7807.9
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 20883.56
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 22795.14
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 30617.22
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 33335.71
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 5563.65
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 8873.39
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 443926.3 | 0.424 | 0.6778 | NA | NA | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
26 DOAS systems with sensible & latent heat recover (erv) - one for each zone (26)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.231 | 24.5801
roof | 0.153 | 37.1111
window | 1.901 | 2.9868
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 11903.3 | 3.14 | 10.72 | 11.3 | 10.64 | Coil:Heating:Electric | 23123.31 | Fan:VariableVolume | 0.75 | 640 | 0.7 | 593.08 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 152509.1 | 2.72 | 9.27 | 9.79 | 9.31 | Coil:Heating:Electric | 291051.97 | Fan:VariableVolume | 0.75 | 640 | 9.28 | 7920.49 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 69199.2 | 2.55 | 8.7 | 9.19 | 8.79 | Coil:Heating:Electric | 130226.7 | Fan:VariableVolume | 0.75 | 640 | 4.21 | 3595.95 | 853.33 | 1
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
No. | Design Size Heating Design Capacity [W]
1 | 12037.17
2 | 181547.93
3 | 66087.97
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 5451.3 | 1.108 | 0.9905 | NA | NA | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.06 | 2207.44 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.231 | 24.5801
roof | 0.153 | 37.1111
window | 1.901 | 2.9868
lighting

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 83896.7 | 2.74 | 9.34 | 9.88 | 9.66 | Coil:Heating:Electric | 194149.92 | Fan:VariableVolume | 0.75 | 640 | 3.61 | 3082.58 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 26461.9 | 2.69 | 9.19 | 9.7 | 9.19 | Coil:Heating:Electric | 56052.92 | Fan:VariableVolume | 0.75 | 640 | 1.68 | 1431.32 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 32411.7 | 2.78 | 9.5 | 10.04 | 9.62 | Coil:Heating:Electric | 69264.65 | Fan:VariableVolume | 0.75 | 640 | 1.77 | 1507.27 | 853.33 | 1
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
No. | Design Size Heating Design Capacity [W]
1 | 62486.58
2 | 11974.04
3 | 18107.87
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2645.2 | 1.31 | 1.1936 | NA | NA | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0.01 | 357.06 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.231 | 24.5801
roof | 0.153 | 37.1111
window | 1.901 | 2.9868
lighting