## school
Secondary School
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 69732.9 | 2.77 | 9.44 | 9.96 | 9.5 | Coil:Heating:Electric | 230697.05 | Fan:VariableVolume | 0.75 | 640 | 4.07 | 3469.16 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 13566.7 | 2.71 | 9.25 | 9.77 | 9.29 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 66246.3 | 2.75 | 9.37 | 9.9 | 9.41 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 66246.3 | 2.54 | 8.66 | 9.14 | 8.76 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 13566.7 | 2.71 | 9.24 | 9.75 | 9.27 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 13749.2 | 2.72 | 9.29 | 9.81 | 9.34 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 68330.8 | 2.6 | 8.89 | 9.39 | 8.99 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 68878.2 | 2.55 | 8.7 | 9.19 | 8.83 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.75 | 640 | 3.98 | 3399.4 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 13749.2 | 2.73 | 9.31 | 9.83 | 9.35 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.75 | 640 | 0.83 | 705.54 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 15502.9 | 2.69 | 9.17 | 9.68 | 9.18 | Coil:Heating:Electric | 55763.03 | Fan:VariableVolume | 0.75 | 640 | 0.98 | 838.55 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 5402.7 | 3.14 | 10.7 | 11.28 | 10.62 | Coil:Heating:Electric | 17358.92 | Fan:VariableVolume | 0.75 | 640 | 0.32 | 271.16 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 64869.7 | 2.57 | 8.77 | 9.26 | 8.87 | Coil:Heating:Electric | 193485.85 | Fan:VariableVolume | 0.75 | 640 | 3.84 | 3277.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 53445.9 | 2.63 | 8.99 | 9.49 | 9.01 | Coil:Heating:Electric | 148420.9 | Fan:VariableVolume | 0.75 | 640 | 3.39 | 2890.88 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 19928.6 | 2.73 | 9.32 | 9.83 | 9.34 | Coil:Heating:Electric | 53911.96 | Fan:VariableVolume | 0.75 | 640 | 1.23 | 1046.48 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 13632.4 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 49034.8 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 14821.8 | 3.14 | 10.72 | 11.3 | 10.64 | Coil:Heating:Electric | 49034.8 | Fan:VariableVolume | 0.75 | 640 | 0.86 | 737.37 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 9875 | 2.69 | 9.2 | 9.71 | 9.21 | Coil:Heating:Electric | 22778.41 | Fan:VariableVolume | 0.75 | 640 | 0.62 | 528.53 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 14050.3 | 2.71 | 9.25 | 9.76 | 9.25 | Coil:Heating:Electric | 29684.18 | Fan:VariableVolume | 0.75 | 640 | 0.89 | 759.98 | 853.33 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 6259.5 | 3.09 | 10.56 | 11.12 | 10.4 | Coil:Heating:Electric | 14095.28 | Fan:VariableVolume | 0.75 | 640 | 0.4 | 338.31 | 853.33 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 59418.6 | 2.63 | 8.96 | 9.46 | 8.99 | Coil:Heating:Electric | 142434.12 | Fan:VariableVolume | 0.75 | 640 | 3.77 | 3213.94 | 853.33 | 6
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
Design Size Heating Design Capacity [W]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 22766.08
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 8809.83
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 26120.14
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 25941.04
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 8834.99
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 10570.39
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 34945.04
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 35076.44
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 10551.96
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 7532.57
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 1322.73
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 30086.89
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 32477.14
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 13929.32
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 3023.7
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 4171.33
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 8579.98
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 11863.34
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 4190.37
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 5325.76
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 14518.86
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 16297.91
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 21194.07
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 24340.41
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 3954.26
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 6364.08
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 443926.3 | 0.424 | 0.6778 | NA | NA | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
26 DOAS systems with sensible & latent heat recover (erv) - one for each zone (26)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.18 | 31.5444
roof | 0.162 | 35.0494
window | 2.101 | 2.7025
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 6650.6 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 13890.83 | Fan:VariableVolume | 0.75 | 640 | 0.42 | 359.73 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 84313.8 | 2.7 | 9.22 | 9.73 | 9.22 | Coil:Heating:Electric | 168807.59 | Fan:VariableVolume | 0.75 | 640 | 5.34 | 4560.52 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 40722.5 | 2.54 | 8.65 | 9.14 | 8.71 | Coil:Heating:Electric | 79149.1 | Fan:VariableVolume | 0.75 | 640 | 2.58 | 2202.67 | 853.33 | 1
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
No. | Design Size Heating Design Capacity [W]
1 | 8861.39
2 | 141768.48
3 | 45096.92
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 5451.3 | 1.108 | 0.9905 | NA | NA | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.06 | 2207.44 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.291 | 19.512
roof | 0.189 | 30.0423
window | 2.101 | 2.7025
lighting

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 55461.8 | 2.56 | 8.75 | 9.24 | 8.8 | Coil:Heating:Electric | 149045.53 | Fan:VariableVolume | 0.75 | 640 | 3.52 | 2999.92 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 22460.4 | 2.7 | 9.21 | 9.73 | 9.22 | Coil:Heating:Electric | 43702.25 | Fan:VariableVolume | 0.75 | 640 | 1.42 | 1214.88 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 25269.2 | 2.71 | 9.26 | 9.77 | 9.25 | Coil:Heating:Electric | 56100.91 | Fan:VariableVolume | 0.75 | 640 | 1.6 | 1366.81 | 853.33 | 1
BASEBOARD:CONVECTIVE:ELECTRIC for each zone
No. | Design Size Heating Design Capacity [W]
1 | 46804.63
2 | 8237.71
3 | 12359.9
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2645.2 | 1.31 | 1.1936 | NA | NA | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0.01 | 357.06 | 0.7
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value
wall | 0.291 | 19.512
roof | 0.189 | 30.0423
window | 2.101 | 2.7025
lighting