## school
Secondary School Victoria BC
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 69974.7 | 2.77 | 9.44 | 9.97 | 9.5 | Coil:Heating:Electric | 230697.05 | Fan:VariableVolume | 0.7 | 640 | 4.07 | 3716.96 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 13433 | 2.71 | 9.24 | 9.75 | 9.27 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 66483.3 | 2.75 | 9.38 | 9.9 | 9.42 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 68019.8 | 2.55 | 8.69 | 9.18 | 8.81 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 13433 | 2.7 | 9.22 | 9.73 | 9.25 | Coil:Heating:Electric | 46917.74 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 14244.2 | 2.72 | 9.27 | 9.79 | 9.31 | Coil:Heating:Electric | 47957.59 | Fan:VariableVolume | 0.7 | 640 | 0.87 | 793.3 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 66043.6 | 2.59 | 8.84 | 9.34 | 8.92 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 63399 | 2.52 | 8.59 | 9.07 | 8.66 | Coil:Heating:Electric | 226058.2 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 14382.5 | 2.72 | 9.29 | 9.81 | 9.32 | Coil:Heating:Electric | 48188.67 | Fan:VariableVolume | 0.7 | 640 | 0.88 | 801.61 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 15530 | 2.69 | 9.18 | 9.68 | 9.18 | Coil:Heating:Electric | 55763.03 | Fan:VariableVolume | 0.7 | 640 | 0.98 | 898.45 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 5299.8 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 17819.82 | Fan:VariableVolume | 0.7 | 640 | 0.34 | 307.14 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 50988.7 | 2.57 | 8.76 | 9.26 | 8.87 | Coil:Heating:Electric | 171429.91 | Fan:VariableVolume | 0.7 | 640 | 3.03 | 2772.82 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 82670.7 | 2.63 | 8.99 | 9.49 | 9.01 | Coil:Heating:Electric | 194872.45 | Fan:VariableVolume | 0.7 | 640 | 5.24 | 4791.05 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 19033.4 | 2.72 | 9.27 | 9.78 | 9.27 | Coil:Heating:Electric | 53402.88 | Fan:VariableVolume | 0.7 | 640 | 1.21 | 1103.05 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 13656.2 | 3.09 | 10.56 | 11.13 | 10.4 | Coil:Heating:Electric | 49034.8 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 14754.3 | 3.14 | 10.71 | 11.29 | 10.63 | Coil:Heating:Electric | 49034.8 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 8410 | 2.69 | 9.18 | 9.69 | 9.19 | Coil:Heating:Electric | 20578.19 | Fan:VariableVolume | 0.7 | 640 | 0.53 | 487.39 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 12003.5 | 2.71 | 9.25 | 9.76 | 9.25 | Coil:Heating:Electric | 26378.22 | Fan:VariableVolume | 0.7 | 640 | 0.76 | 695.64 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 5103.5 | 3.11 | 10.6 | 11.17 | 10.46 | Coil:Heating:Electric | 12068.51 | Fan:VariableVolume | 0.7 | 640 | 0.32 | 289.67 | 914.29 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 53252 | 2.63 | 8.96 | 9.46 | 8.99 | Coil:Heating:Electric | 132473.03 | Fan:VariableVolume | 0.7 | 640 | 3.38 | 3086.13 | 914.29 | 6
electric baseboard for each zone
Design Size Heating Design Capacity [W]
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 363005.2 | 1.008 | 1.5493 | 0.019919 | 22.35 | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
DOAS system with sensible & latent heat recover (erv) - for each zone
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | 90% | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of Stories | Basement?
wall | 0.134 | 42.3731 | 4774.4 |  | No
roof | 0.112 | 50.6964 | 11902
window | 1 | 5.678 | 1193.6
floor |  |  | 19592
stories |  |  |  | 2
lighting
50% reduction

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 7788.3 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 15818.71 | Fan:VariableVolume | 0.72 | 640 | 0.49 | 438.82 | 888.89 | 1
2 | Coil:Cooling:DX:SingleSpeed | 106908.7 | 2.7 | 9.22 | 9.73 | 9.22 | Coil:Heating:Electric | 206338.31 | Fan:VariableVolume | 0.72 | 640 | 6.78 | 6023.62 | 888.89 | 1
3 | Coil:Cooling:DX:SingleSpeed | 47474.3 | 2.54 | 8.65 | 9.14 | 8.71 | Coil:Heating:Electric | 90831.27 | Fan:VariableVolume | 0.72 | 640 | 3.01 | 2674.87 | 888.89 | 1
electric baseboard for each zone
No. | Design Size Heating Design Capacity [W]
1 | 6544.14
2 | 131764.29
3 | 47476.18
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1 | 4473.07 | 0.96 | 13.1 | 0.000245 | 0.27448 | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction |  |  |  | Number of stories
Component | U-value [W/m2-K] | R-Value | Area m2 |  | Basement?
wall | 0.134 | 42.3731 | 1847.77 |  | No
roof | 0.139 | 40.8489 | 4598.25
window | 1.2 | 4.7317 | 649.22
floor |  |  | 4835.1
stories |  |  |  | 1
lighting
40% reduction

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 41765.6 | 2.57 | 8.77 | 9.26 | 8.83 | COIL HEATING ELECTRIC 1 | 123988.4 | Fan:VariableVolume | 0.7 | 640 | 2.61 | 2385 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 18434.1 | 2.7 | 9.21 | 9.73 | 9.22 | COIL HEATING ELECTRIC 2 | 36455.89 | Fan:VariableVolume | 0.7 | 640 | 1.17 | 1068.32 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 20507.7 | 2.71 | 9.26 | 9.77 | 9.25 | COIL HEATING ELECTRIC 3 | 46141.13 | Fan:VariableVolume | 0.7 | 640 | 1.3 | 1188.49 | 914.29 | 1
electric baseboard for each zone
No. | Design Size Heating Design Capacity [W]
1 | 54622.8
2 | 8835.12
3 | 13916.7
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.05 | 2178.06 | 0.96 | 9.43 | 0.000119 | 0.13319 | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0 | 274.66 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.155 | 36.6323 | 876.27 |  | No
roof | 0.142 | 39.9859 | 2090.32
window | 1.2 | 4.7317 | 307.88
floor |  |  | 2090.3
stories |  |  |  | 1
lighting
40% reduction

## highrise
Highrise
3 central DOAS units (with heating & cooling)
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat ( in total)
1 | Coil:Cooling:DX:SingleSpeed | 43581 | 2.68 | 9.16 | 9.67 | 9.17 | Coil:Heating:Electric | 156758.1 | Fan:VariableVolume | 0.6 | 640 | 0.24 | 252.48 | 1066.67 | 79
2 | Coil:Cooling:DX:SingleSpeed | 3734.3 | 2.69 | 9.17 | 9.68 | 9.18 | Coil:Heating:Electric | 13431.98 | Fan:VariableVolume | 0.6 | 640 | 0.24 | 252.48 | 1066.67 | 10
3 (different from previous systems; diff cooling coil type-->) | Coil:Cooling:Water | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Sensible Heat Ratio | Nominal Coil UA Value [W/C] | Nominal Coil Surface Area [m2] | Coil:Heating:Electric | 230.47 | There are 2 Fan:VariableVolume in this unit | 0.6 | 250 | 0.04 | 15.5 | 416.67 | 1 | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
|  | 813 | 596.51 | 0.73 | 95.03 | 0.96 |  |  |  | 0.6 | 1000 | 0.04 | 62.02 | 1666.67 |  | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
electric baseboard for each zone
No. | Design Size Heating Design Capacity [W]
1 | 858.6
2 | 1740.26
3 | 2386.85
4 | 1798.77
5 | 1780.38
6 | 2385.38
7 | 1711.72
8 | 1798.6
9 | 2373.74
10 | 742.68
11 | 730.42
12 | 380.19
13 | 368.92
14 | 742
15 | 380.26
16 | 371.69
17 | 288.83
18 | 281.19
19 | 681.83
20 | 279.38
21 | 682.55
22 | 288.78
23 | 670.42
24 | 706
25 | 670.08
26 | 268.19
27 | 267.33
28 | 676.71
29 | 681.36
30 | 681.94
31 | 276.84
32 | 276.89
33 | 690.45
34 | 700.96
35 | 688.98
36 | 273.13
37 | 700.23
38 | 282.3
39 | 272.89
40 | 282.36
41 | 711.46
42 | 292.58
43 | 722.58
44 | 292.64
45 | 283.47
46 | 283.35
47 | 721.85
48 | 710.54
49 | 744.19
50 | 305.29
51 | 744.9
52 | 305.24
53 | 734.36
54 | 733.38
55 | 296.18
56 | 296.31
57 | 329.05
58 | 772.55
59 | 317.68
60 | 773.27
61 | 760.2
62 | 762
63 | 328.99
64 | 318.02
65 | 371.69
66 | 829.84
67 | 370.62
68 | 382.18
69 | 830.57
70 | 819.06
71 | 812.6
72 | 382.25
73 | 595.17
74 | 1052.88
75 | 584.25
76 | 997.34
77 | 1052.05
78 | 578.82
79 | 595.09
80 | 1042.84
81 | 2509.52
82 | 574.18
83 | 442.58
84 | 409.48
85 | 408.15
86 | 416.08
87 | 427.83
88 | 447.75
89 | 499.37
90 | 738.87
Chilled water loop
Chiller type | Nominal Capacity [W] | Nominal Efficiency [W/W] | IPLV in SI Units [W/W | Design Size Reference Chilled Water Flow Rate [m3/s | Design Size Reference Condenser Fluid Flow Rate [m3/s]
CHILLER WATERCOOLED SCROLL | 568.68 | 4.5 | 5.61 | 2.3e-05 | 2.8e-05
CHILLER WATERCOOLED SCROLL
cooling tower type | Nominal Capacity [W] | Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | U-Factor Times Area Value at Design Air Flow Rate [W/C] | Free Convection Regime Air Flow Rate [m3/s] | Free Convection U-Factor Times Area Value [W/K]
CoolingTower:SingleSpeed | 463.3 | 2.8e-05 | 0.22605 | 21.17 | 0.022605 | 2.12
air cooled variable refrigerant flow (VRF) system with a single outdoor and multiple indoor units
vrf component | Design Size Rated Total Cooling Capacity (gross) [W] | Design Size Rated Total Heating Capacity [W] | Design Size Resistive Defrost Heater Capacity | User-Specified Resistive Defrost Heater Capacity | Design Size Evaporative Condenser Air Flow Rate [m3/s] | Design Size Evaporative Condenser Pump Rated Power Consumption [W]
outdoor unit | 152171.39 | 152171.39 | 152171.39 | 0 | 17.35 | 649.16
terminal units (indoor) largest size shown | Design Size Cooling Supply Air Flow Rate [m3/s] | Design Size Heating Supply Air Flow Rate [m3/s]
indoor unit x 90 (largest size shown) | 0.20206 | 0.20206
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.6667 | 113967.4 | 0.749 | 1.7184 | 0.006252 | 7.02 | 0.000743
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 580545.91 | 0.000743 | 646.5 | 870514.18 | 0.85
1 sensible & latent heat recover (erv)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
2.76 | 2.76 | 90% | 200
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.18 | 31.5444 | 2968.36 |  | No
roof | 0.142 | 39.9859 | 783.65
window | 1 | 5.678 | 886.66
floor |  |  | 7836.5
Stories |  |  |  | 10
lighting
70% reduction