## school
Secondary School Victoria BC
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
Coil:Cooling:DX:SingleSpeed | 97785.8 | 2.66 | 9.06 | 9.59 | 9.42 | Coil:Heating:Gas | 281397.9 | Fan:VariableVolume | 0.7 | 640 | 4.07 | 3716.96 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 19984 | 2.84 | 9.68 | 10.24 | 10.01 | Coil:Heating:Gas | 57329.4 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 759.61 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 95819.5 | 2.65 | 9.05 | 9.58 | 9.4 | Coil:Heating:Gas | 275739.5 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 95819.5 | 2.65 | 9.05 | 9.58 | 9.4 | Coil:Heating:Gas | 275739.5 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 20118.2 | 2.83 | 9.67 | 10.23 | 10 | Coil:Heating:Gas | 57468.52 | Fan:VariableVolume | 0.7 | 640 | 0.84 | 764.72 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 24989.7 | 2.8 | 9.56 | 10.11 | 9.89 | Coil:Heating:Gas | 62519.44 | Fan:VariableVolume | 0.7 | 640 | 1.04 | 949.89 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 95819.5 | 2.74 | 9.37 | 9.91 | 9.71 | Coil:Heating:Gas | 275739.5 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 95819.5 | 2.69 | 9.19 | 9.73 | 9.54 | Coil:Heating:Gas | 275739.5 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 24862.5 | 2.8 | 9.57 | 10.12 | 9.9 | Coil:Heating:Gas | 62387.59 | Fan:VariableVolume | 0.7 | 640 | 1.03 | 945.06 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 23645.7 | 2.84 | 9.68 | 10.24 | 10.01 | Coil:Heating:Gas | 68027.86 | Fan:VariableVolume | 0.7 | 640 | 0.98 | 898.8 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 9091.2 | 3.31 | 11.3 | 11.94 | 11.53 | Coil:Heating:Gas | 22543.45 | Fan:VariableVolume | 0.7 | 640 | 0.38 | 345.57 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 79483.6 | 2.73 | 9.32 | 9.86 | 9.66 | Coil:Heating:Gas | 215923.6 | Fan:VariableVolume | 0.7 | 640 | 3.3 | 3021.27 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 119764 | 2.7 | 9.21 | 9.74 | 9.42 | Coil:Heating:Gas | 238164.1 | Fan:VariableVolume | 0.7 | 640 | 5.98 | 5467.95 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 33849.6 | 2.81 | 9.58 | 10.13 | 9.89 | Coil:Heating:Gas | 68159.89 | Fan:VariableVolume | 0.7 | 640 | 1.45 | 1321.26 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 20784.4 | 2.81 | 9.57 | 10.13 | 9.91 | Coil:Heating:Gas | 59811.29 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 20784.4 | 2.81 | 9.57 | 10.13 | 9.91 | Coil:Heating:Gas | 59811.29 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 13694.3 | 2.77 | 9.46 | 10 | 9.71 | Coil:Heating:Gas | 25900.89 | Fan:VariableVolume | 0.7 | 640 | 0.64 | 585.54 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 18077.9 | 2.76 | 9.43 | 9.96 | 9.61 | Coil:Heating:Gas | 32760.69 | Fan:VariableVolume | 0.7 | 640 | 0.92 | 836.92 | 914.29 | 1
Coil:Cooling:DX:SingleSpeed | 9289.6 | 3.28 | 11.19 | 11.81 | 11.35 | Coil:Heating:Gas | 16023.34 | Fan:VariableVolume | 0.7 | 640 | 0.42 | 379.64 | 914.29 | 2
Coil:Cooling:DX:SingleSpeed | 93543.6 | 2.75 | 9.38 | 9.92 | 9.66 | Coil:Heating:Gas | 170725 | Fan:VariableVolume | 0.7 | 640 | 4.2 | 3842.6 | 914.29 | 6
Hot water baseboard for each zone |  |  |  | Hot water Boiler
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
Hot water pump
|  |  |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 361106.7 | 0.996 | 0.6652 | 0.019919 | 22.35 | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
DOAS system with sensible & latent heat recover (erv) - for each zone
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of Stories | Basement?
wall | 0.134 | 42.3731 | 4476 |  | No
roof | 0.124 | 45.7903 | 11902
window | 1 | 5.678 | 1492
floor |  |  | 19592
stories |  |  |  | 2
lighting

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 10068.5 | 3.2 | 10.92 | 11.52 | 10.94 | Coil:Heating:Gas | 17627.3 | Fan:VariableVolume | 0.7 | 640 | 0.53 | 481.43 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 133288 | 2.74 | 9.35 | 9.88 | 9.46 | Coil:Heating:Gas | 230225.97 | Fan:VariableVolume | 0.7 | 640 | 7.41 | 6776.28 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 59593.7 | 2.55 | 8.7 | 9.2 | 8.86 | Coil:Heating:Gas | 102071.84 | Fan:VariableVolume | 0.7 | 640 | 3.33 | 3040.5 | 914.29 | 1
Hot water baseboard for each zone |  |  |  | Hot water Boiler
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
ZONE HVAC BASEBOARD CONVECTIVE WATER 1 | 0.000125 | 254.68 |  | GAS | 141587.4 | 0.002943 | 96%
ZONE HVAC BASEBOARD CONVECTIVE WATER 3 | 0.002087 | 4262.82 |  | Oil #2 | 141587.4 | 0.002943 | 96
ZONE HVAC BASEBOARD CONVECTIVE WATER 2 | 0.000731 | 1492.53 |  | Hot water pump
|  |  |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
|  |  |  | Pump:VariableSpeed | Intermittent | 179352 | 0.002943 | 885.64 | 300960.01 | 0.86
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 4449.6 | 2.609 | 2.1768 | 0.000245 | 0.27448 | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.099878 | 0.099878 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.155 | 36.6323 | 1822.8 |  | No
roof | 0.126 | 45.0635 | 4598.25
window | 1.1 | 5.1618 | 674.19
floor |  |  | 4835.1
stories |  |  |  | 1
lighting
40% reduction

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 63072.2 | 2.72 | 9.27 | 9.81 | 9.62 | Coil:Heating:Gas | 147539.57 | Fan:VariableVolume | 0.7 | 640 | 2.62 | 2397.45 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 15564 | 2.69 | 9.18 | 9.7 | 9.27 | Coil:Heating:Gas | 31508.15 | Fan:VariableVolume | 0.7 | 640 | 0.9 | 822.32 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 28313.9 | 2.75 | 9.39 | 9.92 | 9.6 | Coil:Heating:Gas | 52872.22 | Fan:VariableVolume | 0.7 | 640 | 1.35 | 1231.26 | 914.29 | 1
hot water baseboard for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 0.000678 | 1391.97 |  | Gas | 104140.58 | 0.000966 | 96%
2 | 0.000114 | 233.59 |  | Hot water pump
3 | 0.000174 | 355.41 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
|  |  |  | Pump:VariableSpeed | Intermittent | 179352 | 0.000966 | 290.79 | 300960 | 0.85
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2166.1 | 3.069 | 2.831 | 0.000119 | 0.13319 | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0 | 274.66 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.137 | 41.4453 | 876.27 |  | No
roof | 0.126 | 45.0635 | 2090.32
window | 1.1 | 5.1618 | 307.88
floor |  |  | 2090.3
stories |  |  |  | 1
lighting
40% reduction

## highrise
Highrise
3 central DOAS units (with heating & cooling)
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Design Size Rated Capacity [W] | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat ( in total)
1 | Coil:Cooling:DX:SingleSpeed | 66445.2 | 2.85 | 9.72 | 10.28 | 10.04 | Coil:Heating:Water | 191209.2 | 0.002856 | 3444.58 | Fan:VariableVolume | 0.72 | 640 | 2.76 | 2455.51 | 888.89 | 79
2 | Coil:Cooling:DX:SingleSpeed | 5693.4 | 2.81 | 9.6 | 10.15 | 9.93 | Coil:Heating:Fuel | 16383.96 | N/A | N/A | Fan:VariableVolume | 0.72 | 640 | 0.24 | 210.4 | 888.89 | 10
3 (different from previous systems) | Coil:Cooling:Water | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Sensible Heat Ratio | Nominal Coil UA Value [W/C] | Nominal Coil Surface Area [m2] | Coil:Heating:Water | 377.74 | 6e-06 | 5.25 | Fan:VariableVolume | 0.72 | 250 | 0.04 | 12.92 | 347.22 | 1 | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
|  | 1422.48 | 1145.47 | 0.64 | 129.65 | 1.32 |  |  |  |  | Fan:VariableVolume | 0.72 | 1000 | 0.04 | 51.68 | 1388.89 |  | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
Hot water baseboard for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 2.4e-05 | 43.51 |  | Gas | 298776.25 | 0.004445 | 96%
2 | 3.4e-05 | 68.72 |  | Hot water pump
3 | 4.4e-05 | 88.77 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
4 | 3.6e-05 | 71.84 |  | Pump:VariableSpeed | Intermittent | 179352 | 0.004445 | 1337.85 | 300960.01 | 0.9
5 | 3.5e-05 | 71.6
6 | 4.4e-05 | 88.88
7 | 1.8e-05 | 34.21
8 | 3.6e-05 | 71.85
9 | 4.4e-05 | 88.79
10 | 2e-05 | 40.31
11 | 2e-05 | 40.27
12 | 1.2e-05 | 24.01
13 | 1.2e-05 | 23.89
14 | 2e-05 | 40.4
15 | 1.2e-05 | 24
16 | 1.2e-05 | 23.98
17 | 1e-05 | 21.26
18 | 1.1e-05 | 21.38
19 | 1.9e-05 | 39.05
20 | 1e-05 | 21.16
21 | 1.9e-05 | 38.94
22 | 1e-05 | 21.26
23 | 1.9e-05 | 38.92
24 | 2e-05 | 40.17
25 | 1.9e-05 | 38.59
26 | 1e-05 | 20.57
27 | 1e-05 | 20.53
28 | 1.9e-05 | 38.77
29 | 1.9e-05 | 38.7
30 | 1.9e-05 | 38.57
31 | 1e-05 | 20.62
32 | 1e-05 | 20.62
33 | 1.9e-05 | 38.74
34 | 1.9e-05 | 38.79
35 | 1.9e-05 | 38.82
36 | 1e-05 | 20.59
37 | 1.9e-05 | 38.92
38 | 1e-05 | 20.68
39 | 1e-05 | 20.59
40 | 1e-05 | 20.67
41 | 1.9e-05 | 39.03
42 | 1e-05 | 20.87
43 | 1.9e-05 | 39.1
44 | 1e-05 | 20.86
45 | 1e-05 | 20.78
46 | 1e-05 | 20.79
47 | 1.9e-05 | 39.24
48 | 1.9e-05 | 39.16
49 | 1.9e-05 | 39.53
50 | 1e-05 | 21.11
51 | 1.9e-05 | 39.42
52 | 1e-05 | 21.12
53 | 1.9e-05 | 39.33
54 | 1.9e-05 | 39.46
55 | 1e-05 | 21.05
56 | 1e-05 | 21.04
57 | 1.1e-05 | 21.59
58 | 2e-05 | 39.98
59 | 1.1e-05 | 21.51
60 | 2e-05 | 39.86
61 | 2e-05 | 39.85
62 | 2e-05 | 39.81
63 | 1.1e-05 | 21.59
64 | 1.1e-05 | 21.52
65 | 1.1e-05 | 23.06
66 | 2e-05 | 41.43
67 | 1.1e-05 | 22.99
68 | 1.1e-05 | 23.14
69 | 2e-05 | 41.3
70 | 2e-05 | 41.25
71 | 2e-05 | 40.88
72 | 1.1e-05 | 23.13
73 | 1.5e-05 | 30.64
74 | 2.4e-05 | 48.01
75 | 1.5e-05 | 30.55
76 | 2.2e-05 | 44.67
77 | 2.4e-05 | 48.13
78 | 1.5e-05 | 30.1
79 | 1.5e-05 | 30.65
80 | 2.4e-05 | 47.97
81 | 4.9e-05 | 98.43
82 | 1.5e-05 | 30.92
83 | 1.3e-05 | 27.37
84 | 1.3e-05 | 26.23
85 | 1.3e-05 | 26.14
86 | 1.3e-05 | 26.25
87 | 1.3e-05 | 26.44
88 | 1.3e-05 | 26.84
89 | 1.4e-05 | 28.3
90 | 1.8e-05 | 36.19
Chilled water loop
Chiller type | Nominal Capacity [W] | Nominal Efficiency [W/W] | IPLV in SI Units [W/W | Design Size Reference Chilled Water Flow Rate [m3/s | Design Size Reference Condenser Fluid Flow Rate [m3/s]
CHILLER WATERCOOLED SCROLL | 1422.45 | 4.5 | 5.61 | 5.6e-05 | 0.000303 | 6.9e-05
CHILLER WATERCOOLED SCROLL
cooling tower type | Nominal Capacity [W] | Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | U-Factor Times Area Value at Design Air Flow Rate [W/C] | Free Convection Regime Air Flow Rate [m3/s] | Free Convection U-Factor Times Area Value [W/K]
CoolingTower:SingleSpeed | 1158.86 | 6.9e-05 | 0.26618 | 53.37 | 0.026618 | 5.34
air cooled variable refrigerant flow (VRF) system with a single outdoor and multiple indoor units
vrf component | Design Size Rated Total Cooling Capacity (gross) [W] | Design Size Rated Total Heating Capacity [W] | Design Size Resistive Defrost Heater Capacity | User-Specified Resistive Defrost Heater Capacity | Design Size Evaporative Condenser Air Flow Rate [m3/s] | Design Size Evaporative Condenser Pump Rated Power Consumption [W]
outdoor unit | 197275.54 | 197275.54 | 197275.54 | 0 | 22.49 | 841.58
terminal units (indoor) largest size shown | Design Size Cooling Supply Air Flow Rate [m3/s] | Design Size Heating Supply Air Flow Rate [m3/s]
indoor unit x 90 (largest size shown) | 0.25527 | 0.25527
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate
Air source heat pump water heater with back up electrical heating element | 2.6667 | 113373.8 | 0.754 | 0.8716 | 0.006252 | 7.02 | 0.000743
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 580545.91 | 0.000743 | 646.5 | 870514.18 | 0.8
3 sensible & latent heat recover (erv) in total - one for each air loop
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
0.2367 | 0.2367 | 90% | 200
0.037209 | 0.037209
2.76 | 2.76
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.18 | 31.5444 | 2929.81 |  | No
roof | 0.142 | 39.9859 | 783.65
window | 1.2 | 4.7317 | 925.21
floor |  |  | 7836.5
Stories |  |  |  | 10
lighting
50% reduction

## Sheet4
|  |  | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h}
1 | Coil:Cooling:DX:SingleSpeed | COIL COOLING DX SINGLE SPEED 1 366KBTU/HR 8.39EER
2 | Coil:Cooling:DX:SingleSpeed | COIL COOLING DX SINGLE SPEED 2 101KBTU/HR 9.44EER
3 | Coil:Cooling:DX:SingleSpeed | COIL COOLING DX SINGLE SPEED 3 124KBTU/HR 9.44EER