## school
Secondary School Victoria BC
fan coil unit - for each zone
Standard Rated Net Cooling Capacity [W] | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP [W/W] | EER [Btu/W-h] | SEER [Btu/W-h] | IEER [Btu/W-h] | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (26 in total
COIL COOLING DX SINGLE SPEED 12 238KBTU/HR 9.26EER | 64137 | 2.72 | 9.29 | 9.81 | 9.29 | Coil:Heating:Electric | 400884 | Fan:VariableVolume | 0.7 | 640 | 4.07 | 3716.96 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 5 87KBTU/HR 9.44EER | 13043.8 | 2.68 | 9.16 | 9.67 | 9.17 | Coil:Heating:Electric | 81529.31 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 9 229KBTU/HR 9.26EER | 62847.4 | 2.72 | 9.28 | 9.8 | 9.28 | Coil:Heating:Electric | 392823 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 10 264KBTU/HR 8.39EER | 62847.4 | 2.51 | 8.58 | 9.06 | 8.64 | Coil:Heating:Electric | 392823 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 16 79KBTU/HR 9.44EER | 13043.8 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 81529.31 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 6 98KBTU/HR 9.44EER | 13043.8 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 81529.31 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 7 377KBTU/HR 8.39EER | 62847.4 | 2.55 | 8.7 | 9.19 | 8.75 | Coil:Heating:Electric | 392823 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 8 260KBTU/HR 8.39EER | 62847.4 | 2.72 | 9.28 | 9.8 | 9.28 | Coil:Heating:Electric | 392823 | Fan:VariableVolume | 0.7 | 640 | 3.98 | 3642.22 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 11 107KBTU/HR 9.44EER | 13043.8 | 2.69 | 9.18 | 9.69 | 9.19 | Coil:Heating:Electric | 81529.31 | Fan:VariableVolume | 0.7 | 640 | 0.83 | 755.93 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 20 78KBTU/HR 9.44EER | 15502.9 | 2.69 | 9.17 | 9.67 | 9.17 | Coil:Heating:Electric | 96899.83 | Fan:VariableVolume | 0.7 | 640 | 0.98 | 898.45 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 18 38KBTU/HR 14.0SEER | 4674 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 29214.22 | Fan:VariableVolume | 0.7 | 640 | 0.3 | 270.87 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 15 319KBTU/HR 8.39EER | 47508.9 | 2.53 | 8.62 | 9.11 | 8.68 | Coil:Heating:Electric | 296951.1 | Fan:VariableVolume | 0.7 | 640 | 3.01 | 2753.3 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 17 512KBTU/HR 8.39EER | 40505.1 | 2.56 | 8.73 | 9.22 | 8.79 | Coil:Heating:Electric | 205137.8 | Fan:VariableVolume | 0.7 | 640 | 2.57 | 2347.41 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 13 130KBTU/HR 9.44EER | 11444.5 | 2.7 | 9.21 | 9.72 | 9.22 | Coil:Heating:Electric | 71532.76 | Fan:VariableVolume | 0.7 | 640 | 0.73 | 663.24 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 3 51KBTU/HR 14.0SEER | 13632.4 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 85208.14 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 4 51KBTU/HR 14.0SEER | 13632.4 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 85208.14 | Fan:VariableVolume | 0.7 | 640 | 0.86 | 790.04 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 14 81KBTU/HR 9.44EER | 8148.7 | 2.69 | 9.18 | 9.69 | 9.18 | Coil:Heating:Electric | 29380.95 | Fan:VariableVolume | 0.7 | 640 | 0.52 | 472.24 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 19 120KBTU/HR 9.44EER | 10243.5 | 2.7 | 9.22 | 9.73 | 9.22 | Coil:Heating:Electric | 32683.1 | Fan:VariableVolume | 0.7 | 640 | 0.65 | 593.64 | 914.29 | 1
COIL COOLING DX SINGLE SPEED 1 43KBTU/HR 14.0SEER | 5413.7 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 17971.45 | Fan:VariableVolume | 0.7 | 640 | 0.34 | 313.74 | 914.29 | 2
COIL COOLING DX SINGLE SPEED 2 494KBTU/HR 8.39EER | 54576.4 | 2.57 | 8.76 | 9.25 | 8.81 | Coil:Heating:Electric | 195782.8 | Fan:VariableVolume | 0.7 | 640 | 3.46 | 3162.89 | 914.29 | 6
hot water baseboard for each zone |  |  |  | Hot water Boiler
| Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 18 | 0.000341 | 694.63 |  | Oil #2 | 595602.81 | 0.005687 | 96%
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 11 | 0.000105 | 214.52 |  | Hot water pump
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 15 | 0.00034 | 690.33 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 16 | 0.000338 | 687.83 |  | Pump:VariableSpeed | Intermittent | 179352 | 0.005687 | 1711.55 | 300959.99 | 0.9
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 22 | 0.000106 | 214.91
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 12 | 0.000133 | 270.63
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 13 | 0.000468 | 954.47
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 14 | 0.000469 | 956.32
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 17 | 0.000133 | 270.35
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 26 | 0.000142 | 289.2
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 24 | 3.9e-05 | 78.66
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 21 | 0.000506 | 1028.83
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 23 | 0.000466 | 948.43
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 19 | 0.000235 | 478.79
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 9 | 4.8e-05 | 98.35
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 10 | 6.4e-05 | 130.6
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 20 | 0.000129 | 262.91
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 25 | 0.00017 | 346.91
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 1 | 5.8e-05 | 117.63
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 2 | 7.3e-05 | 149.59
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 4 | 0.000235 | 479.33
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 5 | 0.000233 | 474.79
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 3 | 0.000318 | 648.27
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 6 | 0.000353 | 720.85
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 7 | 7.8e-05 | 159.42
ZONE HVAC BASEBOARD CONVECTIVE ELECTRIC 8 | 0.000107 | 217.32
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 2.0282 | 360963.3 | 0.992 | 1.5449 | 0.019919 | 22.35 | 0.00074
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1070524 | 0.00074 | 1174.27 | 1586666.67 | 0.86
DOAS system with sensible & latent heat recover (erv) - for each zone
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | Efficiency | Pressure drop (Pa)
4.07 | 4.07 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.8268 | 0.8268
3.98 | 3.98
3.98 | 3.98
0.8268 | 0.8268
0.98267 | 0.98267
0.29627 | 0.29627
3.01 | 3.01
1.9 | 1.9
0.72542 | 0.72542
0.86411 | 0.86411
0.86411 | 0.86411
0.22431 | 0.22431
0.22431 | 0.22431
0.064008 | 0.064008
0.064008 | 0.064008
0.34747 | 0.34747
0.29261 | 0.29261
0.34747 | 0.34747
0.29261 | 0.29261
0.10424 | 0.10424
0.10424 | 0.10424
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of Stories | Basement?
wall | 0.11 | 51.6182 | 5490.56 |  | No
roof | 0.095 | 59.7684 | 11902
window | 0.7 | 8.1114 | 477.44
floor |  |  | 19592
stories |  |  |  | 2
lighting
60% reduction

## warehouse
Warehouse
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 4997.7 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 15319.24 | Fan:VariableVolume | 0.75 | 640 | 0.32 | 270.32 | 853.33 | 1
2 | Coil:Cooling:DX:SingleSpeed | 90573.9 | 2.59 | 8.84 | 9.33 | 8.88 | Coil:Heating:Electric | 217792.1 | Fan:VariableVolume | 0.75 | 640 | 5.74 | 4899.13 | 853.33 | 1
3 | Coil:Cooling:DX:SingleSpeed | 34318.9 | 2.73 | 9.3 | 9.81 | 9.29 | Coil:Heating:Electric | 86096.23 | Fan:VariableVolume | 0.75 | 640 | 2.18 | 1856.3 | 853.33 | 1
hot water baseboard for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 0.000115 | 231.3 |  | Oil #2 | 127625.34 | 0.003206 | 96%
2 | 0.002254 | 4108.3 |  | Oil #2 | 127625.34 | 0.003206 | 96
3 | 0.000837 | 1688.44 |  | Hot water pump
|  |  |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
|  |  |  | Pump:VariableSpeed | Intermittent | 179352 | 0.003206 | 964.78 | 300960.01 | 0.86
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.1043 | 4447.4 | 13.128 | 1.7591 | 0.000245 | 0.27448 | 2.6e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 1205.26 | 2.6e-05 | 0.04 | 1698.03 | 0.91
3 DOAS system with sensible & latent heat recover (erv) -one for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.099878 | 0.099878
0.97684 | 0.97684
0.42471 | 0.42471
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.137 | 41.4453 | 2297.23 |  | No
roof | 0.126 | 45.0635 | 4598.25
window | 0.7 | 8.1114 | 199.76
floor |  |  | 4835.1
stories |  |  |  | 1
lighting
50% reduction

## retailstripmal
Retail strip mall
3 Fan coil unit for 3 zones
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Nominal Total Capacity [W] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat (3 in total)
1 | Coil:Cooling:DX:SingleSpeed | 35521.4 | 2.54 | 8.67 | 9.16 | 8.73 | COIL HEATING ELECTRIC 1 | 191622.5 | Fan:VariableVolume | 0.7 | 640 | 2.25 | 2058.59 | 914.29 | 1
2 | Coil:Cooling:DX:SingleSpeed | 9707.4 | 2.68 | 9.15 | 9.66 | 9.16 | COIL HEATING ELECTRIC 2 | 30681.2 | Fan:VariableVolume | 0.7 | 640 | 0.62 | 562.58 | 914.29 | 1
3 | Coil:Cooling:DX:SingleSpeed | 11035.8 | 2.69 | 9.19 | 9.7 | 9.2 | COIL HEATING ELECTRIC 3 | 47806.55 | Fan:VariableVolume | 0.7 | 640 | 0.7 | 639.56 | 914.29 | 1
electric baseboard for each zone |  |  | Hot water Boiler
No. | Design Size Heating Design Capacity [W] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 54622.8 |  | Oil #2 | 93694.16 | 0.000915 | 96%
2 | 8835.12 |  | Oil #2 | 0.001 | 0.000915 | 96
3 | 13916.7 |  | Hot water pump
|  |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
|  |  | Pump:VariableSpeed | Intermittent | 179352 | 0.005949 | 1790.49 | 300959.99 | 0.9
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Air source heat pump water heater with back up electrical heating element | 0.050625 | 2165.2 | 3.04 | 2.6246 | 0.000119 | 0.13319 | 1.5e-05
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 194.95 | 1.5e-05 | 0 | 274.66 | 0.91
3 DOAS system with sensible & latent heat recover (erv) - for each zone (3)
Design Size Supply Air Flow Rate [m3/s] | Design Size Exhaust Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
1.83 | 1.83 | sensible effectiveness @ 100% heating = 0.76 sensible effectiveness @ 100% cooling = 0.76 sensible effectiveness @ 75% heating = 0.81 sensible effectiveness @ 75% cooling = 0.81 latent effectiveness @ 75% cooling = 0.75 latent effectiveness @ 75% heating = 0.75 latent effectiveness @ 100% cooling = 0.75 latent effectiveness @ 100% heating = 0.75 | 200
0.20353 | 0.20353
0.40706 | 0.40706
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.122 | 46.541 | 1065.74 |  | No
roof | 0.124 | 45.7903 | 2090.32
window | 0.8 | 7.0975 | 118.41
floor |  |  | 2090.3
stories |  |  |  | 1
lighting
50% reduction

## highrise
Highrise
3 central DOAS units (with heating & cooling)
No. | Component Type | Standard Rating (Net) Cooling Capacity {W} | Standard Rated Net COP {W/W} | EER {Btu/W-h} | SEER {Btu/W-h} | IEER {Btu/W-h} | Heating Type | Design Size Rated Capacity [W] | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] | Fan Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Air Flow Rate [m3/s] | Rated Electric Power [W] | Rated Power Per Max Air Flow Rate [W-s/m3] | VAV Terminal Box - No Reheat ( in total)
1 | Coil:Cooling:DX:SingleSpeed | 43581 | 2.64 | 9.01 | 9.51 | 9.03 | Coil:Heating:Water | 272399.73 | 0.004069 | 4191.93 | Fan:VariableVolume | 0.75 | 640 | 2.76 | 2357.29 | 853.33 | 79
2 | Coil:Cooling:DX:SingleSpeed | 8277.5 | 3.09 | 10.55 | 11.12 | 10.4 | Coil:Heating:Electric | 30521.79 | N/A | N/A | Fan:VariableVolume | 0.75 | 640 | 0.52 | 447.73 | 853.33 | 10
3 (different from previous systems; diff cooling coil type-->) | Coil:Cooling:Water | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Sensible Heat Ratio | Nominal Coil UA Value [W/C] | Nominal Coil Surface Area [m2] | Coil:Heating:Electric | 1903.5 | N/A |  | There are 2 Fan:VariableVolume in this unit | 0.3 | 250 | 0.1 | 83.54 | 833.4 | 1 | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
|  | 2218.82 | 1596.94 | 0.72 | 257.4 | 2.61 | [5 empty] | 0.55 | 1000 | 0.1 | 182.27 | 1818.3 |  | General | VICTORIA INTL AP ANN HTG 99.6% CONDNS DB | 2019-12-21 07:00
hot water baseboard for each zone |  |  |  | Hot water Boiler
No. | Design Size Maximum Water Flow Rate [m3/s] | Design Size U-Factor Times Area Value [W/K] |  | Fuel | User-Specified Nominal Capacity | Design Size Design Water Flow Rate | Thermal efficiency
1 | 2.7e-05 | 49 |  | Oil #2 | 454292.78 | 0.005949 | 92%
2 | 4.4e-05 | 89.56 |  | Hot water pump
3 | 5.4e-05 | 108.8 |  | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor Efficiency [W/W]
4 | 4.5e-05 | 89.91 |  | Pump:VariableSpeed | Intermittent | 179352 | 0.005949 | 1790.49 | 300959.99 | 0.9
5 | 4.4e-05 | 89.56
6 | 5.4e-05 | 108.94
7 | 5.4e-05 | 108.6
8 | 4.5e-05 | 89.91
9 | 5.4e-05 | 108.46
10 | 2.1e-05 | 43.65
11 | 2.1e-05 | 43.45
12 | 1.2e-05 | 24.76
13 | 1.2e-05 | 24.44
14 | 2.1e-05 | 43.74
15 | 1.2e-05 | 24.75
16 | 1.2e-05 | 24.55
17 | 1.2e-05 | 23.56
18 | 1.2e-05 | 23.45
19 | 2.2e-05 | 43.89
20 | 1.1e-05 | 23.2
21 | 2.1e-05 | 43.77
22 | 1.2e-05 | 23.57
23 | 2.1e-05 | 43.53
24 | 2.2e-05 | 44.81
25 | 2.2e-05 | 43.84
26 | 1.1e-05 | 23.26
27 | 1.1e-05 | 23.21
28 | 2.2e-05 | 44.03
29 | 2.2e-05 | 44.2
30 | 2.2e-05 | 44.07
31 | 1.2e-05 | 23.6
32 | 1.2e-05 | 23.59
33 | 2.2e-05 | 44.4
34 | 2.2e-05 | 44.72
35 | 2.2e-05 | 44.49
36 | 1.2e-05 | 23.69
37 | 2.2e-05 | 44.86
38 | 1.2e-05 | 24.1
39 | 1.2e-05 | 23.69
40 | 1.2e-05 | 24.09
41 | 2.2e-05 | 44.99
42 | 1.2e-05 | 24.61
43 | 2.2e-05 | 45.35
44 | 1.2e-05 | 24.6
45 | 1.2e-05 | 24.17
46 | 1.2e-05 | 24.17
47 | 2.2e-05 | 45.49
48 | 2.2e-05 | 45.13
49 | 2.3e-05 | 46.1
50 | 1.2e-05 | 25.13
51 | 2.3e-05 | 45.95
52 | 1.2e-05 | 25.14
53 | 2.2e-05 | 45.59
54 | 2.2e-05 | 45.73
55 | 1.2e-05 | 24.69
56 | 1.2e-05 | 24.69
57 | 1.3e-05 | 25.89
58 | 2.3e-05 | 46.89
59 | 1.3e-05 | 25.46
60 | 2.3e-05 | 46.74
61 | 2.3e-05 | 46.51
62 | 2.3e-05 | 46.37
63 | 1.3e-05 | 25.9
64 | 1.3e-05 | 25.45
65 | 1.4e-05 | 27.53
66 | 2.4e-05 | 48.74
67 | 1.4e-05 | 27.54
68 | 1.4e-05 | 27.98
69 | 2.4e-05 | 48.6
70 | 2.4e-05 | 48.23
71 | 2.4e-05 | 48.38
72 | 1.4e-05 | 27.97
73 | 1.8e-05 | 37.24
74 | 2.8e-05 | 56.6
75 | 1.8e-05 | 36.8
76 | 2.8e-05 | 56.38
77 | 2.8e-05 | 56.74
78 | 1.8e-05 | 36.81
79 | 1.8e-05 | 37.25
80 | 2.8e-05 | 56.23
81 | 6.1e-05 | 123.3
82 | 1.5e-05 | 30.95
83 | 1.4e-05 | 28.99
84 | 1.4e-05 | 28.34
85 | 1.4e-05 | 28.5
86 | 1.4e-05 | 28.78
87 | 1.4e-05 | 29.12
88 | 1.5e-05 | 29.71
89 | 1.6e-05 | 31.65
90 | 2e-05 | 41.6
Chilled water loop
Chiller type | Nominal Capacity [W] | Nominal Efficiency [W/W] | IPLV in SI Units [W/W | Design Size Reference Chilled Water Flow Rate [m3/s | Design Size Reference Condenser Fluid Flow Rate [m3/s]
CHILLER WATERCOOLED SCROLL | 4597.34 | 4.5 | 5.6 | 19.14 | 0.000224
CHILLER WATERCOOLED SCROLL
cooling tower type | Nominal Capacity [W] | Design Water Flow Rate [m3/s] | Design Air Flow Rate [m3/s] | U-Factor Times Area Value at Design Air Flow Rate [W/C] | Free Convection Regime Air Flow Rate [m3/s] | Free Convection U-Factor Times Area Value [W/K]
CoolingTower:SingleSpeed | 3745.43 | 0.000224 | 0.19696 | 207.69 | 0.019696 | 20.77
air cooled variable refrigerant flow (VRF) system with a single outdoor and multiple indoor units
vrf component | Design Size Rated Total Cooling Capacity (gross) [W] | Design Size Rated Total Heating Capacity [W] | Design Size Resistive Defrost Heater Capacity | User-Specified Resistive Defrost Heater Capacity | Design Size Evaporative Condenser Air Flow Rate [m3/s] | Design Size Evaporative Condenser Pump Rated Power Consumption [W]
outdoor unit | N/A | N/A | N/A | N/A | N/A | N/A
terminal units (indoor) largest size shown | Design Size Cooling Supply Air Flow Rate [m3/s] | Design Size Heating Supply Air Flow Rate [m3/s]
indoor unit x 90 (largest size shown) | N/A | N/A
Main service water heating
Water heater | Volume {m3} | Maximum Capacity {W} | Standard Rated Recovery Efficiency | Standard Rated Energy Factor | Condenser water flow rate [m3/s] | Evaporator air flow rate [m3/s] | Use Side Design Flow Rate [m3/s]
Electric water heater | 2.6667 | 139339.1 | 0.315 | 0.716 | N/A | N/A | 0.000743
Pump | Type | Control | Head [pa] | Water Flow [m3/s] | Electric Power [W] | Power Per Water Flow Rate [W-s/m3] | Motor efficiency
SERVICE WATER LOOP PUMP | Pump:ConstantSpeed | Intermittent | 580545.91 | 0.000743 | 646.5 | 870514.18 | 0.85
Construction
Component | U-value [W/m2-K] | R-Value | Area m2 | Number of stories | Basement?
wall | 0.155 | 36.6323 | 3469.52 |  | No
roof | 0.114 | 49.807 | 783.65
window | 1.4 | 4.0557 | 385.5
floor |  |  | 7836.5
Stories |  |  |  | 10
lighting
40% reduction
1 sensible & latent heat recover (erv)
Name of erv | Design Size Nominal Supply Air Flow Rate [m3/s] | 1 set of Efficiency | Pressure drop (Pa)
ALL_ST=OFFICE ENCLOSED <= 25 M2_FL=BUILDING STORY 1_SCH=A ERV HX | 0.037209 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 10_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 1_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 2_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 3_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 4_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 5_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 6_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 7_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 8_SCHG 7 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 1 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 2 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 3 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 4 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 5 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 6 ERV HX | 0.034968 | 90% | 200
DU_BT=SPACE FUNCTION_ST=DWELLING UNITS GENERAL_FL=BUILDING STORY 9_SCHG 7 ERV HX | 0.034968 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 10_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 1_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 2_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 3_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 4_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 5_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 6_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 7_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 8_SCH=G ERV HX | 0.02367 | 90% | 200
WILD_ST=CORRIDOR/TRANSITION AREA OTHER-SCH-G_FL=BUILDING STORY 9_SCH=G ERV HX | 0.02367 | 90% | 200
Packaged air conditioner (ea unit contains heat & cool coils; use cool coil flowrate as design flowrate)
Type | Coil Type | Coil Final Gross Total Capacity [W] | Coil Final Reference Air Volume Flow Rate [m3/s]
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1901.81 | 0.11489
| COIL:HEATING:ELECTRIC | 5546.313 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 2314.501 | 0.13982
| COIL:HEATING:ELECTRIC | 6185.601 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1909.16 | 0.11533
| COIL:HEATING:ELECTRIC | 5557.708 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1901.677 | 0.11488
| COIL:HEATING:ELECTRIC | 5546.105 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 2317.356 | 0.13999
| COIL:HEATING:ELECTRIC | 6190.024 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 2310.075 | 0.13955
| COIL:HEATING:ELECTRIC | 6178.743 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1909.294 | 0.11534
| COIL:HEATING:ELECTRIC | 5557.916 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 2307.222 | 0.13938
| COIL:HEATING:ELECTRIC | 6174.323 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 951.601 | 0.057486
| COIL:HEATING:ELECTRIC | 4054.035 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1216.716 | 0.073502
| COIL:HEATING:ELECTRIC | 4047.6 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 826.14 | 0.049907
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 859.827 | 0.051942
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1161.692 | 0.070178
| COIL:HEATING:ELECTRIC | 4057.144 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 817.797 | 0.049403
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 862.733 | 0.052118
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 855.417 | 0.051676
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 917.87 | 0.055449
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1174.132 | 0.070929
| COIL:HEATING:ELECTRIC | 4061.768 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 918.691 | 0.055498
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 960.446 | 0.058021
| COIL:HEATING:ELECTRIC | 4057.815 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 861.789 | 0.052061
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1248.571 | 0.075426
| COIL:HEATING:ELECTRIC | 4050.098 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1084.258 | 0.0655
| COIL:HEATING:ELECTRIC | 4092.174 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1256.515 | 0.075906
| COIL:HEATING:ELECTRIC | 4060.012 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 924.284 | 0.055836
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 929.597 | 0.056157
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1041.154 | 0.062896
| COIL:HEATING:ELECTRIC | 4066.312 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1184.316 | 0.071545
| COIL:HEATING:ELECTRIC | 4071.793 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 971.569 | 0.058693
| COIL:HEATING:ELECTRIC | 4067.544 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 874.529 | 0.05283
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 868.305 | 0.052454
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1032.227 | 0.062357
| COIL:HEATING:ELECTRIC | 4078.118 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 971.095 | 0.058664
| COIL:HEATING:ELECTRIC | 4088.85 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1256.415 | 0.0759
| COIL:HEATING:ELECTRIC | 4081.202 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 924.205 | 0.055831
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1185.164 | 0.071596
| COIL:HEATING:ELECTRIC | 4093.373 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 876.26 | 0.052935
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 930.532 | 0.056213
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 869.996 | 0.052556
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1028.763 | 0.062148
| COIL:HEATING:ELECTRIC | 4097.413 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 875.599 | 0.052895
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 980.41 | 0.059227
| COIL:HEATING:ELECTRIC | 4109.449 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 869.32 | 0.052516
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 922.938 | 0.055755
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 929.5 | 0.056151
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1183.725 | 0.071509
| COIL:HEATING:ELECTRIC | 4114.08 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1254.402 | 0.075778
| COIL:HEATING:ELECTRIC | 4101.989 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1182.053 | 0.071408
| COIL:HEATING:ELECTRIC | 4133.734 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 868.328 | 0.052456
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 993.329 | 0.060007
| COIL:HEATING:ELECTRIC | 4129.091 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 874.615 | 0.052835
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1026.371 | 0.062003
| COIL:HEATING:ELECTRIC | 4117.133 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1252.27 | 0.07565
| COIL:HEATING:ELECTRIC | 4121.716 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 928.252 | 0.056076
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 921.635 | 0.055676
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 867.7 | 0.052418
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1180.717 | 0.071327
| COIL:HEATING:ELECTRIC | 4159.718 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 927.322 | 0.05602
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1010.315 | 0.061033
| COIL:HEATING:ELECTRIC | 4154.915 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1250.489 | 0.075542
| COIL:HEATING:ELECTRIC | 4147.339 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1024.58 | 0.061895
| COIL:HEATING:ELECTRIC | 4142.579 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 873.987 | 0.052798
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 920.696 | 0.055619
| COIL:HEATING:ELECTRIC | 3499.065 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 922.388 | 0.055721
| COIL:HEATING:ELECTRIC | 3524.916 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1181.927 | 0.0714
| COIL:HEATING:ELECTRIC | 4220.394 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 928.978 | 0.05612
| COIL:HEATING:ELECTRIC | 3525.222 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 876.241 | 0.052934
| COIL:HEATING:ELECTRIC | 3539.721 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1050.29 | 0.063448
| COIL:HEATING:ELECTRIC | 4215.688 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1042.394 | 0.062971
| COIL:HEATING:ELECTRIC | 4203.685 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1251.28 | 0.07559
| COIL:HEATING:ELECTRIC | 4208.377 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 869.974 | 0.052555
| COIL:HEATING:ELECTRIC | 3539.415 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 894.153 | 0.054016
| COIL:HEATING:ELECTRIC | 3843.673 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1222.758 | 0.073867
| COIL:HEATING:ELECTRIC | 4477.865 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 947.129 | 0.057216
| COIL:HEATING:ELECTRIC | 3829.416 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1280.487 | 0.077354
| COIL:HEATING:ELECTRIC | 4470.629 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1225.85 | 0.074054
| COIL:HEATING:ELECTRIC | 4482.566 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 954.158 | 0.057641
| COIL:HEATING:ELECTRIC | 3829.698 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 901.024 | 0.054431
| COIL:HEATING:ELECTRIC | 3843.953 | -999
Packaged air conditioner (heating & cooling) | COIL:COOLING:DX:SINGLESPEED | 1214.908 | 0.073393
| COIL:HEATING:ELECTRIC | 4465.932 | -999